## DOOR_AND_FRAME_SCHED_0
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
DOOR AND INTERIOR OPENING SCHEDULE
NUMBER | FIRE RATING (MINUTES) | SIZE |  | DOOR |  |  | FRAME |  |  | HARDWARE SET | GLASS FILM | GLASS TYPE | SPECIAL NOTES AND COMMENTS
|  | WIDTH | HEIGHT | ELEVATION | MATERIAL | FINISH | ELEVATION | MATERIAL | FINISH
N101A |  | 6' - 0" | 8' - 9 1/2" | FG | AL & G | AL - Clear Anodized |  | AL | AL - Clear Anodized | AL-11 | N/A | GL-3 | EXTERIOR STOREFRONT SYSTEM - REFER TO ELEVATIONS
N101B |  | 6' - 0" | 7' - 9 1/2" | FG | AL & G | AL - Clear Anodized |  | AL | AL - Clear Anodized | AL-10 | GL-1 | GL-1 | INTERIOR STOREFRONT SYSTEM - REFER TO ELEVATIONS
N104 |  | 3' - 0" | 7' - 8" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-01 | GLF-2 | GL-5
N104A |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-04 | GLF-1 | GL-5
N104B |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-04 | GLF-1 | GL-5
N104C |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-04 | GLF-1 | GL-5
N104D |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-05 | GLF-1 | GL-5
N104E |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-04 | GLF-1 | GL-5
N104F |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-05 | GLF-1 | GL-5
N105A | 45 | 3' - 0" | 7' - 8" | FG | AL & G | AL - Clear Anodized | DF | AL | AL - Clear Anodized | AL-09 | GLF-2 | GL-6
N105B | 45 | 3' - 0" | 7' - 8" | FG | AL & G | AL - Clear Anodized | DF | AL | AL - Clear Anodized | AL-09 | GLF-2 | GL-6
N106A | 45 | 3' - 0" | 7' - 8" | FG | AL & G | AL - Clear Anodized | DF | AL | AL - Clear Anodized | AL-09 | GLF-2 | GL-6
N106B | 45 | 3' - 0" | 7' - 8" | FG | AL & G | AL - Clear Anodized | DF | AL | AL - Clear Anodized | AL-09 | GLF-2 | GL-6
N107B |  | 6' - 0" | 7' - 0" | F | WD | WV-1 | A | HM | P-1C | 205 | N/A | N/A
N108 |  | 3' - 0" | 7' - 0" | F | WD | WV-1 | A | HM | P-1C | 203 | N/A | N/A
N109 |  | 3' - 0" | 7' - 0" | F | WD | WV-1 | A | HM | P-1C | 202 | N/A | N/A
N110 |  | 3' - 0" | 7' - 8" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-06 | GLF-2 | GL-5
N111 |  | 3' - 0" | 7' - 8" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-06 | GLF-2 | GL-5
N112A | 45 | 3' - 0" | 7' - 8" | FG | AL & G | AL - Clear Anodized | DF | AL | AL - Clear Anodized | AL-09 | GLF-2 | GL-6
N112B | 45 | 3' - 0" | 7' - 8" | FG | AL & G | AL - Clear Anodized | DF | AL | AL - Clear Anodized | AL-09 | GLF-2 | GL-6
N114 |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-07 | GLF-2 | GL-5
N115 |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-07 | GLF-2 | GL-5
N116 |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-07 | GLF-2 | GL-5
N117 |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-07 | GLF-2 | GL-5
N118 |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-07 | GLF-2 | GL-5
N119 |  | 6' - 0" | 7' - 0" | F | WD | WV-1 | A | HM | P-1C | 205 | N/A | N/A
N119B |  | 6' - 0" | 7' - 0" | F | WD | WV-1 | A | HM | P-1C | 204 | N/A | N/A
N120 |  | 3' - 0" | 7' - 0" | F | WD | WV-1 | A | HM | P-1C | 203 | N/A | N/A
N120A |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-04 | GLF-1 | GL-5
N120C |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-02 | GLF-1 | GL-5
N120CA |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-04 | GL-1 | GL-5
N120D |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-04 | GLF-1 | GL-5
N120E |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-04 | GLF-1 | GL-5
N120F |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-04 | GLF-1 | GL-5
N120G |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-04 | GLF-1 | GL-5
N120H |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-04 | GLF-1 | GL-5
N120J |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-04 | GLF-1 | GL-5
N120K |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-04 | GLF-1 | GL-5
N121 |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-04 | GLF-1 | GL-5
N123 |  | 3' - 0" | 7' - 0" | F | WD | WV-1 | A | HM | P-1C | 201 | N/A | N/A
N124 |  | 3' - 0" | 7' - 0" | F | WD | WV-1 | A | HM | P-1C | 207 | N/A | N/A
N138 |  | 3' - 0" | 7' - 0" | N | WD | WV-1 | A | HM | P-1C | 200 | N/A | GL-5
N140 | 45 | 3' - 0" | 7' - 0" | F | WD | WV-1 | AF | HM | P-1C | 203 | N/A | N/A
NE180B |  | 6' - 0" | 7' - 0" | (E) | (E) | (E) | (E) | (E) | (E) | EX-01 | (E) | (E) | EXISTING DOOR. PROVIDE CARD READER.
S101 |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-12 | GLF-2 | GL-5
S101A |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-03 | GLF-2 | GL-5
S102A |  | 3' - 0" | 7' - 0" | F | PAINTED MASONITE | P-1C | A | HM | P-1C | 206 | N/A | N/A
S102B |  | 3' - 0" | 7' - 0" | F | PAINTED MASONITE | P-1C | A | HM | P-1C | 200 | N/A | N/A
S102C |  | 3' - 0" | 7' - 0" | F | PAINTED MASONITE | P-1C | A | HM | P-1C | 206 | N/A | N/A
S103 |  | 3' - 0" | 7' - 0" | F | PAINTED MASONITE | P-1C | A | HM | P-1C | 206 | N/A | N/A
S105 | 45 | 3' - 0" | 7' - 0" | F | PAINTED MASONITE | P-1C | AF | HM | P-1C | 203 | N/A | N/A
S107A |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-08 | GLF-2 | GL-5
S107B |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-08 | GLF-2 | GL-5
S108 |  | 5' - 11" | 7' - 10" | FG | AL & G | AL - Clear Anodized | A | AL | AL - Clear Anodized | AL-13 | GLF-1 | GL-5
S108A |  | 6' - 0" | 7' - 0" | F | PAINTED MASONITE | P-1C | A | MTL | P-1C | 208 | N/A | N/A
S108B |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-04 | GLF-1 | GL-5
S108C |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-04 | GLF-1 | GL-5
S108D |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-04 | GLF-1 | GL-5
S108E |  | 3' - 0" | 7' - 10" | FG | AL & G | AL - Clear Anodized | D1 | AL | AL - Clear Anodized | AL-04 | GLF-1 | GL-5
S109 |  | 3' - 0" | 7' - 0" | F | PAINTED MASONITE | P-1C | A | HM | P-1C | 209 | N/A | N/A

## PLUMBING_SCHEDULES_1_0
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
PLUMBING FIXTURE SCHEDULE (FLUSH VALVES)
FIXTURE TAG | DESCRIPTION | TYPE | CODE FLOW REQUIREMENTS | DESIGN FIXTURE FLOW | MANUFACTURER | MODEL | FLUSH-VALVE MANUFACTURER | FLUSH-VALVE MODEL | PLUMBING REMARKS
WC-1 | WATER CLOSET - WALL MOUNTED - ADA | MANUAL | 1.6 GPF | 1.1/1.6 GPF | AMERICAN STANDARD | 3351.101 | SLOAN | WES 111-1.6/1.1 | FIXTURE SHALL BE WATERSENSE LABELED. PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.
WC-2 | WATER CLOSET - WALL MOUNTED - ADA | MANUAL | 1.6 GPF | 1.28 GPF | AMERICAN STANDARD | 3351.101 | SLOAN | ROYAL 111-1.6 | VITREOUS CHINA. PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.
U-1 | URINAL - WALL MOUNTED | MANUAL | 1 GPF | 0.125 GPF | ZURN | Z5755-U | SLOAN | ROYAL 186-0.125-DBP | VITREOUS CHINA, WALL-MOUNT. PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.

## PLUMBING_SCHEDULES_1_1
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
PLUMBING FIXTURE SCHEDULE (SINKS)
TAG | DESCRIPTION | TYPE | DESIGN FIXTURE FLOW | SERVICE CONNECTION | [5 empty] | FIXTURE UNIT CALCULATIONS |  |  |  |  | MANUFACTURER | MODEL | FAUCET MANUFACTURER | FAUCET MODEL | REMARKS
|  |  |  | COLD WATER |  |  | TRAP | WASTE PIPE | VENT PIPE | QUANTI TY | WASTE CALCULATIONS |  | DOMESTIC WATER CALCULATIONS
[11 empty] | DFU EACH | TOTAL FU | WSFU EACH | TOTAL FU
KS-1 | KITCHEN SINK - UNDERMOUNT | MANUAL | 1.5 GPM | 3/4" |  |  | 2" | 2" | 2" | 1 | 2 | 2 | 1.4 | 4 | ELKAY | ELUHAD211550 | DELTA | D26C3934 | WITHOUT PERFECT DRAIN. PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.
L-1 | LAVATORY - UNDERMOUNT | HARD-WIRED | 0.5 GPM |  | 1/2" |  | 2" | 2" | 2" | 5 | 1 | 1 | 2 | 2 | AMERICAN STANDARD | 0496.300 | CHICAGO FAUCET | EQ-A12C-23ABCP | PROVIDE ASSE 1070 DEVICE. PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.
L-2 | LAVATORY - UNDERMOUNT | HARD-WIRED | 0.5 GPM | 1/2" | 1/2" |  | 2" | 2" | 2" | 14 | 1 | 1 | 2 | 2 | AMERICAN STANDARD | 0496.300 | CHICAGO FAUCET | EQ-A12C-23ABCP | REFER TO ARCH SHEET G.2.4.0 MEN AND WOMEN RESTROOM ALTERNATES. PROVIDE ASSE 1070 DEVICE. PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.
MS-1 | MOP SINK - FLOOR MOUNTED (RELOCATED) | MANUAL | N/A |  | 3/4" |  | 2" | 3" | 2" | 1 | 2 | 2 | 3 | 3 | REFER TO ARCH PLANS | N/A | N/A | N/A | PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.

## PLUMBING_SCHEDULES_1_2
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
PLUMBING ELECTRIC WATER HEATER SCHEDULE
TAG | SYSTEM | LOCATION | TEMP RISE | ELECTRICAL |  |  |  | BASIS OF DESIGN |  | REMARKS
|  |  |  | AMPS | W | VOLTAGE | PHASE | MANUFACTURER | MODEL
DWH-1 | DOMESTIC WATER HEATER | JANITORS ROOM N108 | 72 °F | 14.4 | 6000 W | 208 V | 3 | AO SMITH | DEN-30 | PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.
EWH-1 | INSTANTANEOUS WATER HEATER | BREAKROOM N138 | 73 °F | 58 | 16050 W | 277 V | 1 | CHRONOMITE | R-58L/277 | PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.

## PLUMBING_SCHEDULES_1_3
0 | 1 | 2 | 3 | 4 | 5 | 6
PLUMBING GARBAGE DISPOSAL SCHEDULE
TAG | DESCRIPTION | ELECTRICAL DATA |  | MANUFACTURER | MODEL | REMARKS
|  | VOLTAGE | PHASE
GD-1 | GARBAGE DISPOSAL | 120 V | 1 | INSINKERATOR | BADGER 5 | PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.

## PLUMBING_SCHEDULES_1_4
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
PLUMBING FIXTURE SCHEDULE (MISCELLANEOUS)
TAG | DESCRIPTION | DESIGN FIXTURE FLOW |  |  | SERVICE CONNECTIONS | [6 empty] | MANUFACTURER | MODEL | REMARKS
[5 empty] | COLD WATER | HOT WATER |  |  | TRAP | WASTE PIPE | VENT PIPE
DF-1 | DRINKING FOUNTAIN WITH BOTTLE FILLER |  | N/A |  | 1/2" |  | N/A |  | 1 1/2" | 2" | 2" | ELKAY | EZSTLG8WSLK | PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.
DF-2 | DRINKING FOUNTAIN |  | N/A |  | 1/2" |  | N/A |  | 1 1/2" | 2" | 2" | ELKAY | EZSTLG8LC | PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.

## PLUMBING_SCHEDULES_1_5
0 | 1
MINIMUM TRAP DEPTH
DRAW THRU UNIT | X = (FAN T.S.P. ÷ 2) + 1"
BLOW THRU UNIT | X = FAN T.S.P. + 1"

## MECHANICAL_DETAILS_&_0
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28
COMPUTER ROOM AIR-CONDITIONING UNIT SCHEDULE
TAG | AREA SERVED | FAN DATA |  |  |  | COOLING COIL DATA | [5 empty] | MAX FACE VELOCITY (FPM) | CONDENSER |  |  |  | HUMIDIFIER DATA |  |  | FILTER DATA | ELECTRICAL DATA |  |  | OPERATING WEIGHT (IBS) |  | BASIS OF DESIGN |  | REMARKS
|  | AIRFLOW (CFM) | ESP (INWG) | QTY | TYPE | TOTAL CAPACITY (MBH) | SENSIBLE CAPACITY (MBH) | EAT DB (F) | EAT WB (F) | LAT DB (F) | LAT WB (F) |  | TAG | MODEL | DESIGN AMBIENT (F) | MANUFACTURER | TYPE | CAPACITY (LBS/HR) | ELECTRICAL POWER (KW) |  | MAX kW AT DESIGN | VOLTAGE | PHASE | INDOOR UNIT | OUTDOOR UNIT | MANUFACTURER | MODEL
CRAC-1 | SERVER ROOM | 9200 | 0.20 | 1 | ECM | 241 | 173 | 75 | 62 | 54 | 52 | 380 | CU-4 | MCL110E8 | 95 | LIEBERT | INFRARED | 22 | 9.6 | 4" MERV 8 | 21 | 460 V | 3 | 1900 | 602 | LIEBERT | VS070AD | 1,2,3,4,5
CRAC-2 | SERVER ROOM | 9200 | 0.20 | 1 | ECM | 241 | 173 | 75 | 62 | 54 | 52 | 380 | CU-5 | MCL110E8 | 95 | LIEBERT | INFRARED | 22 | 9.6 | 4" MERV 8 | 21 | 460 V | 3 | 1900 | 602 | LIEBERT | VS070AD | 1,2,3,4,5

## MECHANICAL_DETAILS_&_1
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
ROOF TOP UNIT SCHEDULE
TAG | INDOOR FAN DATA | [6 empty] | HEATING SECTION |  |  |  | COOLING COIL DATA | [5 empty] | ELECTRICAL DATA |  |  |  |  | BASIS OF DESIGN |  | REMARKS
| MIN. OA (CFM) | TOTAL AIRFLOW (CFM) | DESIGN AIRFLOW (CFM) | EXTERNAL STATIC PRESSURE (IN WG) | FAN SPEED (RPM) | MOTOR |  | HEATING TYPE | OUTPUT HEATING CAPACITY (MBH) | EAT DB (F) | LAT DB (F) | EAT DB (F) | EAT WB (F) | LAT DB (F) | LAT WB (F) | SENSIBLE COOLING (MBH) | TOTAL COOLING (MBH) | V/PH/HZ | FLA |  | MCA | MOP | MODEL | MANUFACTURER
[6 empty] | BHP | HP | [11 empty] | INDOOR FAN | OUTDOOR FAN
(E)RTU-03 | 1750 | 11000 | 5100 | 1 | 661 | - | 10 | GAS HEAT | 369 | 70 | 111 | 80 | 63 | 58 | 54 | 223 | 276 | 460/3/60 | 9.8 | 3.5 | 76.46 | 90 | YCD-330 | TRANE | 1
(E)RTU-04 | 5400 | 18000 | 14900 | 1 | 662 | - | 15 | GAS HEAT | 461 | 70 | 101 | 80 | 63 | 58 | 54 | 394 | 492 | 460/3/60 | 18 | 3.5 | 125.27 | 150 | YCD-600 | TRANE | 1

## MECHANICAL_DETAILS_&_2
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
GRILLE, REGISTER, AND DIFFUSER SCHEDULE
TAG | SYSTEM | TYPE | FACE SIZE | LINEAR DATA |  |  | DISCHARGE SOUND (NC) | MATERIAL | BASIS OF DESIGN |  | REMARKS
|  |  |  | SLOT QUANTITY | SLOT WIDTH (INCH) | SLOT LENGTH (FT) |  |  | MANUFACTURER | MODEL
E1 | EXHAUST | PERFORATED | 24X24 |  |  |  | 25 | STEEL | TITUS | PAR | 1,2
E2 | EXHAUST | PERFORATED | 12X12 |  |  |  | 25 | STEEL | TITUS | PAR | 1,2
R1 | RETURN | PERFORATED | 24X24 |  |  |  | 25 | STEEL | TITUS | PAR | 1,2
R2 | RETURN | LINEAR | PER PLAN | 1 | 2 | 4 | 25 | STEEL | TITUS | FL-20 | 1,2,3,5
R3 | RETURN | SIDEWALL | PER PLAN |  |  |  | 25 | STEEL | TITUS | 350R | 1,2
S1 | SUPPLY | PLAQUE | 24X24 |  |  |  | 25 | STEEL | TITUS | PAR | 1,2
S2 | SUPPLY | LINEAR | PER PLAN | 1 | 1 | 4 | 25 | STEEL | TITUS | FL-10 | 1.2.3.4
S3 | SUPPLY | LINEAR | PER PLAN | 1 | 2 | 4 | 25 | STEEL | TITUS | FL-20 | 1,2,3,4
S4 | SUPPLY | LINEAR | PER PLAN | 1 | 2 | 5 | 25 | STEEL | TITUS | FL-20 | 1,2,3,4
S5 | SUPPLY | SIDEWALL | PER PLAN |  |  |  | 25 | STEEL | TITUS | 300R | 1,2
S6 | SUPPLY | PLAQUE | 24X24 |  |  |  | 25 | STEEL | TITUS | T3SQ-2 | 1,2,6

## MECHANICAL_DETAILS_&_3
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26
FAN SCHEDULE
TAG | AREA SERVED | LOCATION | AIRFLOW (CFM) | TYPE | ESP (IN WG) | FAN SPEED (RPM) | MOTOR |  |  |  | EMERGENCY POWER | SOUND POWER LEVEL AT FAN INLET (dB) | [7 empty] | LwA | dBA | SONES | WEIGHT (LBS) | BASIS OF DESIGN |  | REMARKS
[7 empty] | BHP | HP | SPEED CONTROL | V/PH/HZ |  | OCTAVE BAND NO. | [11 empty] | MANUFACTURER | MODEL
[12 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
EF-1 | RESTROOM N141 & N142 | ROOF | 850 | CENTRIFUGAL | 0.5 | 1550 | 0.15 | 0.25 | ECM | 115/60/1 | NO | 73 | 76 | 76 | 68 | 63 | 62 | 57 | 51 | 72 | 60 | 10.5 | 37 | GREENHECK | G-099-VG | 1,2,3,4

## MECHANICAL_DETAILS_&_4
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
SILENCER SCHEDULE
TAG | SYSTEM | VELOCITY (FPM) | MAX AIR PD (IN.W.G) | LENGTH (IN) | DYNAMIC INSERTION LOSS BY OCTAVE BAND (DB RE 10^(-12)) W | [7 empty] | BASIS OF DESIGN |  | REMARKS
[5 empty] | 1 (63 HZ) | 2 (125 HZ) | 3 (250 HZ) | 4 (500 HZ) | 5 (1,000 HZ) | 6 (2,000 HZ) | 7 (4,000 HZ) | 8 (8,000 HZ) | MANUFACTURER | MODEL
SIL-1 | RETURN | 1130 | 0.07 | 36 | 4 | 10 | 15 | 20 | 24 | 21 | 12 | 11 | IAC | 24NS36
SIL-2 | RETURN | 1020 | 0.05 | 36 | 4 | 10 | 15 | 20 | 24 | 21 | 12 | 11 | IAC | 24NS36
SIL-3 | RETURN | 1740 | 0.23 | 60 | 6 | 12 | 19 | 27 | 28 | 15 | 15 | 13 | IAC | 5LFL 36X36

## MECHANICAL_DETAILS_&_5
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
UNIT HEATER SCHEDULE
TAG | SYSTEM | LOCATION | AIRSIDE DATA |  |  | HEATING DATA | [5 empty] | MOTOR DATA |  |  |  | OPERATING WEIGHT (IBS) | FILTER | BASIS OF DESIGN |  | REMARKS
|  |  | HIGH SPEED (CFM) | EAT (F) | LAT (F) | CAPACITY (MBH) | ROWS | EWT (F) | LWT (F) | FLOW (GPM) | FLUID PD (FT H2O) | TYPE | HP | V/PH/HZ | FLA |  |  | MANUFACTURER | MODEL
CUH-1 | HEATING | VESTIBULE | 490 | 35 | 108 | 30.7 | 1 | 180 | 160 | 3.2 | 0.80 | ECM | 0.25 | 120/1/60 | 1.12 | 115.00 | 1" MERV 8 | RITTLING | RFRC-420-04 | 1

## MECHANICAL_DETAILS_&_6
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
SPLIT SYSTEM AIR-COOLED CONDITIONING UNIT SCHEDULE (INDOOR)
TAG | LOCATION | CONFIGURATION | INDOOR AIRFLOW | ESP | MOTOR OUTPUT (W) | COOLING COIL DATA |  | HEATING COIL DATA |  | VOLTAGE | PHASE | MCA | UNIT WEIGHT (IBS) | BASIS OF DESIGN |  |  | REMARKS
[6 empty] | TOTAL CAPACITY (MBH) | SENSIBLE CAPACITY (MBH) | TOTAL CAPACITY (MBH) | POWER (KW) |  |  |  |  | MANUFACTURER | INDOOR MODEL | OUTDOOR MODEL
FCU-1 | ELEC E-1-S21 | DUCTLESS WALL MOUNTED | 425 | 0.25 | 30 | 18.0 | 13.9 | 9.9 | 1.7 | 208 | 1 | 1.0 | 29.00 | MITSUBISHI | TPKA0A0181HA70A | TRUZA0181KA70NA | 1
FCU-2 | ELEC N140 | DUCTLESS WALL MOUNTED | 775 | 0.25 | 56 | 30.0 | 23.3 | 14.8 | 2 | 208 | 1 | 1.0 | 46.00 | MITSUBISHI | TPKA0A0301KA70A | TRUZA0301HA70NA | 1
FCU-3 | DATA N124 | DUCTED | 1450 | 0.25 | 244 | 42.0 | 36.2 | 25.1 | 3 | 208 | 1 | 3.5 | 91.00 | MITSUBISHI | PEAD-42AA7 | PUZ-A42NKA7-BS | 1

## MECHANICAL_DETAILS_&_7
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
SPLIT SYSTEM AIR-COOLED CONDENSING UNIT SCHEDULE (OUTDOOR)
TAG | ASSOCIATED INDOOR UNIT TAG | LOCATION | REFRIGERANT | NOMINAL CAPACITY (BTUH) | AMBIENT TEMP (F) | ELECTRICAL DATA |  |  |  | EER | OPERATING WEIGHT (LBS) | BASIS OF DESIGN |  | REMARKS
[6 empty] | VOLTAGE (V) | PHASE | MCA (A) | MOCP (A) |  |  | MANUFACTURER | MODEL
CU-1 | FCU-1 | ROOF | R410A | 18000 | 95 | 208 | 1 | 11.0 | 28 | 9.9 | 100 | MITSUBISHI | TRUZA0181KA70NA | 1,2
CU-2 | FCU-2 | ROOF | R410A | 30000 | 95 | 208 | 1 | 19.0 | 26 | 9.5 | 153 | MITSUBISHI | TRUZA0301HA70NA | 1,2
CU-3 | FCU-3 | ROOF | R410A | 42000 | 95 | 208 | 1 | 25.0 | 31 | 10.7 | 215 | MITSUBISHI | PUZ-A42NKA7-BS | 1,2

## MECHANICAL_DETAILS_&_8
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
VOLUME CONTROL BOX SCHEDULE
TAG | INLET SIZE | VAV BOX SIZE MAX (CFM) | OUTLET SIZE | DESIGN AIRFLOW |  |  | MAX AIR PD (INWG) | MIN INLET SP (IN WG) | REHEAT COIL DATA | [6 empty] | MAX WATER PD (FT) | DISCHARGE SOUND (NC) | BASIS OF DESIGN |  | REMARKS
|  |  |  | MAX AIRFLOW (CFM) | MIN AIRFLOW (CFM) | REHEAT AIRFLOW (CFM) |  |  | EAT (F) | LAT(F) | EWT (F) | LWT (F) | SENSIBLE CAPACITY (MBH) | FLOW (GPM) | ROWS |  |  | MANUFACTURER | MODEL
VAV-S-1 | 10 | 1400 | 14x12 | 850 | 275 | 275 | 2 | 0.50 | 55 | 87 | 180 | 160 | 8.0 | 0.5 | 1 | 0.07 | 25 | TITUS | DESV | 1,2
VAV-S-2 | 10 | 1400 | 14x12 | 800 | 250 | 250 | 2 | 0.50 | 55 | 87 | 180 | 160 | 8.6 | 0.6 | 1 | 0.07 | 25 | TITUS | DESV | 1,2
VAV-S-3 | 12 | 2000 | 16x15 | 1425 | 450 | 450 | 2 | 0.50 | 55 | 90 | 180 | 160 | 14.0 | 0.8 | 1 | 0.13 | 25 | TITUS | DESV | 1,2
VAV-S-4 | 12 | 2000 | 16x15 | 1425 | 450 | 450 | 2 | 0.50 | 55 | 90 | 180 | 160 | 14.0 | 0.8 | 1 | 0.13 | 25 | TITUS | DESV | 1,2
VAV-S-5 | 8 | 800 | 12x10 | 725 | 225 | 225 | 2 | 0.50 | 55 | 90 | 180 | 160 | 6.5 | 0.3 | 1 | 0.12 | 25 | TITUS | DESV | 1,2
VAV-S-6 | 10 | 1400 | 14x12 | 1200 | 375 | 375 | 2 | 0.50 | 55 | 90 | 180 | 160 | 21.0 | 0.9 | 2 | 0.10 | 25 | TITUS | DESV | 1,2
VAV-S-7 | 10 | 1400 | 14x12 | 1200 | 375 | 375 | 2 | 0.50 | 55 | 90 | 180 | 160 | 21.0 | 0.9 | 2 | 0.10 | 25 | TITUS | DESV | 1,2
VAV-S-8 | 6 | 400 | 12x8 | 300 | 100 | 100 | 2 | 0.50 | 55 | 92 | 180 | 160 | 4.0 | 0.3 | 1 | 0.08 | 25 | TITUS | DESV | 1,2
VAV-S-9 | 8 | 800 | 12x10 | 400 | 125 | 125 | 2 | 0.50 | 55 | 92 | 180 | 160 | 5.0 | 0.3 | 1 | 0.10 | 25 | TITUS | DESV | 1,2
VAV-S-10 | 8 | 800 | 12x10 | 400 | 125 | 125 | 2 | 0.50 | 55 | 90 | 180 | 160 | 5.0 | 0.3 | 1 | 0.00 | 25 | TITUS | DESV | 1,2
VAV-U-1 | 8 | 800 | 12x10 | 700 | 225 | 225 | 2 | 0.50 | 55 | 90 | 180 | 160 | 8.1 | 0.7 | 1 | 0.29 | 25 | TITUS | DESV | 1,2
VAV-U-2 | 8 | 800 | 12x10 | 650 | 200 | 200 | 2 | 0.50 | 55 | 90 | 180 | 160 | 7.5 | 0.6 | 1 | 0.21 | 25 | TITUS | DESV | 1,2
VAV-U-3 | 8 | 800 | 12x10 | 750 | 225 | 225 | 2 | 0.50 | 55 | 90 | 180 | 160 | 7.7 | 0.5 | 1 | 0.20 | 25 | TITUS | DESV | 1,2
VAV-U-4 | 8 | 800 | 12x10 | 750 | 225 | 225 | 2 | 0.50 | 55 | 90 | 180 | 160 | 8.4 | 0.8 | 1 | 0.42 | 25 | TITUS | DESV | 1,2
VAV-U-5 | 8 | 800 | 12x10 | 600 | 200 | 200 | 2 | 0.50 | 55 | 90 | 180 | 160 | 6.5 | 0.4 | 1 | 0.17 | 25 | TITUS | DESV | 1,2
VAV-U-6 | 12 | 2000 | 16x15 | 1525 | 800 | 800 | 2 | 0.50 | 55 | 90 | 180 | 160 | 27.3 | 1.0 | 2 | 0.13 | 25 | TITUS | DESV | 1,2
VAV-U-7 | 8 | 800 | 12x10 | 600 | 200 | 200 | 2 | 0.50 | 55 | 90 | 180 | 160 | 6.5 | 0.4 | 1 | 0.17 | 25 | TITUS | DESV | 1,2
VAV-U-8 | 8 | 800 | 12x10 | 600 | 200 | 200 | 2 | 0.50 | 55 | 89 | 180 | 160 | 6.5 | 0.4 | 1 | 0.17 | 25 | TITUS | DESV | 1,2
VAV-U-9 | 8 | 800 | 12x10 | 550 | 175 | 175 | 2 | 0.50 | 55 | 89 | 180 | 160 | 5.4 | 0.3 | 1 | 0.10 | 25 | TITUS | DESV | 1,2
VAV-U-10 | 10 | 1400 | 14x12 | 1225 | 375 | 375 | 2 | 0.50 | 55 | 87 | 180 | 160 | 7.5 | 0.6 | 1 | 0.21 | 25 | TITUS | DESV | 1,2
VAV-U-11 | 12 | 2000 | 16x15 | 1700 | 550 | 550 | 2 | 0.50 | 55 | 85 | 180 | 160 | 16.0 | 0.9 | 2 | 0.17 | 25 | TITUS | DESV | 1,2
VAV-U-12 | 6 | 400 | 12x8 | 125 | 100 | 100 | 2 | 0.50 | 55 | 93 | 180 | 160 | 4.0 | 0.3 | 1 | 0.08 | 25 | TITUS | DESV | 1,2
VAV-U-13 | 6 | 400 | 12x8 | 275 | 100 | 100 | 2 | 0.50 | 55 | 93 | 180 | 160 | 4.0 | 0.3 | 1 | 0.08 | 25 | TITUS | DESV | 1,2
VAV-U-14 | 6 | 400 | 12x8 | 250 | 100 | 100 | 2 | 0.50 | 55 | 94 | 180 | 160 | 4.0 | 0.3 | 1 | 0.08 | 25 | TITUS | DESV | 1,2
VAV-U-15 | 8 | 800 | 12x10 | 600 | 200 | 200 | 2 | 0.50 | 55 | 90 | 180 | 160 | 6.8 | 0.4 | 1 | 0.16 | 25 | TITUS | DESV | 1,2
VAV-U-16 | 6 | 400 | 12x8 | 125 | 100 | 100 | 2 | 0.50 | 55 | 98 | 180 | 160 | 3.5 | 0.3 | 1 | 0.08 | 25 | TITUS | DESV | 1,2
VAV-U-17 | 6 | 800 | 12x8 | 250 | 100 | 100 | 2 | 0.50 | 55 | 93 | 180 | 160 | 4.0 | 0.3 | 1 | 0.08 | 25 | TITUS | DESV | 1,2
VAV-U-18 | 8 | 800 | 12x10 | 500 | 150 | 150 | 2 | 0.50 | 55 | 89 | 180 | 160 | 5.4 | 0.3 | 1 | 0.10 | 25 | TITUS | DESV | 1,2
VAV-U-19 | 8 | 800 | 12x10 | 500 | 150 | 150 | 2 | 0.50 | 55 | 89 | 180 | 160 | 5.4 | 0.3 | 1 | 0.10 | 25 | TITUS | DESV | 1,2
VAV-U-20 | 8 | 800 | 12x10 | 500 | 150 | 150 | 2 | 0.50 | 55 | 89 | 180 | 160 | 5.4 | 0.3 | 1 | 0.10 | 25 | TITUS | DESV | 1,2
VAV-U-21 | 8 | 800 | 12x10 | 600 | 600 | 600 | 2 | 0.50 | 55 | 85 | 180 | 160 | 20.5 | 0.9 | 2 | 0.20 | 25 | TITUS | DESV | 1,2
VAV-U-22 | 8 | 800 | 12x10 | 600 | 200 | 200 | 2 | 0.50 | 55 | 87 | 180 | 160 | 6.8 | 0.4 | 1 | 0.17 | 25 | TITUS | DESV | 1,2
VAV-U-23 | 8 | 800 | 12x10 | 300 | 100 | 100 | 2 | 0.50 | 55 | 89 | 180 | 160 | 5.4 | 0.3 | 1 | 0.10 | 25 | TITUS | DESV | 1,2
VAV-U-24 | 10 | 1400 | 14x12 | 975 | 300 | 300 | 2 | 0.50 | 55 | 90 | 180 | 160 | 10.3 | 0.9 | 2 | 0.10 | 25 | TITUS | DESV | 1,2
VAV-U-25 | 10 | 1400 | 14x12 | 1000 | 1000 | 1000 | 2 | 0.50 | 55 | 90 | 180 | 160 | 34.2 | 1.8 | 2 | 0.22 | 25 | TITUS | DESV | 1,2
VAV-U-26 | 8 | 800 | 12x10 | 400 | 150 | 150 | 2 | 0.50 | 55 | 90 | 180 | 160 | 5.4 | 0.3 | 1 | 0.10 | 25 | TITUS | DESV | 1,2
VAV-U-27 | 8 | 800 | 12x10 | 450 | 150 | 150 | 2 | 0.50 | 55 | 90 | 180 | 160 | 5.4 | 0.3 | 1 | 0.10 | 25 | TITUS | DESV | 1,2
VAV-U-28 | 12 | 2000 | 16x15 | 1500 | 450 | 450 | 2 | 0.50 | 55 | 90 | 180 | 160 | 14.4 | 0.9 | 2 | 0.14 | 25 | TITUS | DESV | 1,2
VAV-U-29 | 10 | 1200 | 14x12 | 1000 | 300 | 300 | 2 | 0.50 | 55 | 87 | 180 | 160 | 9.6 | 0.9 | 2 | 0.08 | 25 | TITUS | DESV | 1,2
VAV-U-30 | 10 | 1200 | 14x12 | 850 | 850 | 850 | 2 | 0.50 | 55 | 87 | 180 | 160 | 29.1 | 1.4 | 2 | 0.00 | 25 | TITUS | DESV | 1,2

## MECHANICAL_EQUIPMENT_0
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
MECHANICAL EQUIPMENT SCHEDULE
TAG | PANEL | CIRCUIT NUMBER | INPUT POWER | VOLTAGE | PHASE | TOTAL POWER LOAD | MOTOR RATED SWITCH | VFD | DISC. SWITCH |  | PHASE & NEUTRAL |  |  | GROUND |  | CONDUIT |  | COMMENTS
[9 empty] | AMPS | POLES | SETS | NO. OF WIRES | AWG | NO. OF WIRES | AWG | SETS | SIZE
CRAC-1 | ISACHA | 25,27,29 | 23725 W | 480 V | 3 | 23725 VA | No | No | 100 A | 3 | 1 | 3 | #4 | 1 | #8 | 1 | 1''
CRAC-2 | ISACHA | 31,33,35 | 23725 W | 480 V | 3 | 23725 VA | No | No | 100 A | 3 | 1 | 3 | #4 | 1 | #8 | 1 | 1''
CU-1 | UCCSLB | 18,20 | 2288 W | 208 V | 1 | 2288 VA | No | No | 30 A | 2 | 1 | 2 | #10 | 1 | #10 | 1 | 3/4''
CU-2 | UCCSLB | 22,24 | 3952 W | 208 V | 1 | 3952 VA | No | No | 30 A | 2 | 1 | 2 | #10 | 1 | #10 | 1 | 3/4''
CU-3 | UCCSLB | 26,28 | 4160 W | 208 V | 1 | 4160 VA | No | No | 30 A | 2 | 1 | 2 | #10 | 1 | #10 | 1 | 3/4''
CU-4 | ISACHA | 26,28,30 | 1163 W | 480 V | 3 | 1163 VA | No | No | 30 A | 3 | 1 | 3 | #12 | 1 | #12 | 1 | 3/4''
CU-5 | ISACHA | 32,34,36 | 1163 W | 480 V | 3 | 1163 VA | No | No | 30 A | 3 | 1 | 3 | #12 | 1 | #12 | 1 | 3/4''
CUH-1 | UCCSLB | 16 | 696 W | 120 V | 1 | 696 VA | Yes | No |  |  | 1 | 2 | #12 | 1 | #12 | 1 | 3/4''
EF-1 | UCCSLB | 30 | 696 W | 120 V | 1 | 696 VA | Yes | No |  |  | 1 | 2 | #12 | 1 | #12 | 1 | 3/4''
EWH-1 | ISACHA | 23 | 16066 W | 277 V | 1 | 16066 VA | No | No | 100 A | 2 | 1 | 2 | #4 | 1 | #8 | 1 | 1''
VAV-ZONE-A | UCCSLB | 2 | 750 W | 120 V | 1 | 750 VA | No | No |  |  | 1 | 2 | #12 | 1 | #12 | 1 | 3/4'' | 24V TRANSFORMER PROVIDED BY DIV 23, UNIT EQUIPPED WITH INTEGRAL DISCONNECT SWITCH
VAV-ZONE-B | UCCSLB | 4 | 750 W | 120 V | 1 | 750 VA | No | No |  |  | 1 | 2 | #12 | 1 | #12 | 1 | 3/4'' | 24V TRANSFORMER PROVIDED BY DIV 23, UNIT EQUIPPED WITH INTEGRAL DISCONNECT SWITCH
VAV-ZONE-C | UCCSLB | 6 | 750 W | 120 V | 1 | 750 VA | No | No |  |  | 1 | 2 | #12 | 1 | #12 | 1 | 3/4'' | 24V TRANSFORMER PROVIDED BY DIV 23, UNIT EQUIPPED WITH INTEGRAL DISCONNECT SWITCH
VAV-ZONE-D | UCCSLB | 8 | 750 W | 120 V | 1 | 750 VA | No | No |  |  | 1 | 2 | #12 | 1 | #12 | 1 | 3/4'' | 24V TRANSFORMER PROVIDED BY DIV 23, UNIT EQUIPPED WITH INTEGRAL DISCONNECT SWITCH
VAV-ZONE-E | UCCSLB | 10 | 750 W | 120 V | 1 | 750 VA | No | No |  |  | 1 | 2 | #12 | 1 | #12 | 1 | 3/4'' | 24V TRANSFORMER PROVIDED BY DIV 23, UNIT EQUIPPED WITH INTEGRAL DISCONNECT SWITCH
VAV-ZONE-ISAC | ISACLA | 2 | 750 W | 120 V | 1 | 750 VA | No | No |  |  | 1 | 2 | #12 | 1 | #12 | 1 | 3/4'' | 24V TRANSFORMER PROVIDED BY DIV 23, UNIT EQUIPPED WITH INTEGRAL DISCONNECT SWITCH

## LIGHTING_FIXTURE_&_C_0
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
LIGHTING FIXTURE SCHEDULE
TYPE | DESCRIPTION | MANUFACTURER | MODEL | LOAD | WATTS PER FOOT (FOR CONTINUOUS RUNS) | LAMP | DRIVER | VOLTAGE | MOUNTING | COMMENTS | TYPE
L2A | 4"x22' LINEAR PENDANT, DIRECT/INDIRECT, LED, 810/910 LUMEN PF, 4000K, DIM TO 1% | PEERLESS LIGHTING | OPM4 LLP 22FT MSL8 80CRI 40K I910LMF 810LMF DARK ZT 277 DCT F1/ | 299 VA | 14 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | MOUNT @ 10'-0" AFF TO BOTTOM OF FIXTURE | L2A
L2B | 4"x16' LINEAR PENDANT, DIRECT/INDIRECT, LED, 810/910 LUMEN PF, 4000K, DIM TO 1% | PEERLESS LIGHTING | OPM4 LLP 16FT MSL8 80CRI 40K I910LMF 810LMF DARK ZT 277 DCT F1/ | 218 VA | 14 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | MOUNT @ 10'-0" AFF TO BOTTOM OF FIXTURE | L2B
L3A | 4" SQUARE DOWNLIGHT, LED, 1500 LUMEN, 4000K, DIM TO 1% | GOTHAM LIGHTING | EVO4SQ 40/15 AR LSS MVOLT GZ1 | 14 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L3A
L3B | 6" SQUARE DOWNLIGHT, LED, 2500 LUMEN, 4000K, DIM TO 1% | GOTHAM LIGHTING | EVO4SQ 40/25 AR LSS MVOLT GZ1 | 26 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L3B
L4A | 4" WIDE PERIMETER WALL-TO-WALL LINEAR RECESSED, ASSYMETRIC, LED, 875 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | P43-PSTD FLSH LED4 SO R(PER PLANS) TMW AWL D1R WTW SC X3B UNV DM01 |  | 10 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED | REFER TO LIGHTING PLANS FOR REQUIRED LENGTH | L4A
L4B | 4" WIDE PERIMETER WALL-TO-POCKET LINEAR RECESSED, ASSYMETRIC, LED, 875 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | P43-PSTD FLSH LED4 SO R(PER PLANS) TMW AWL D1R WTW/LP SC X3B UNV DM01 |  | 10 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED | REFER TO LIGHTING PLANS FOR REQUIRED LENGTH | L4B
L5A | 2'x4' ARCHITECTURAL RECESSED TROFFER, LED, 3000 LUMEN, 4000K, DIM TO 1% | MARK ARCHITECTURAL LIGHTING | WHSPR LCTR 2X4 80CRI 40K 3000LM MIN1 277 SWC ZT | 30 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L5A
L5B | 2'x4' ARCHITECTURAL RECESSED TROFFER, LED, 4000 LUMEN, 4000K, DIM TO 1% | MARK ARCHITECTURAL LIGHTING | WHSPR LCTR 2X4 80CRI 40K 4000LM MIN1 277 SWC ZT | 34 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L5B
L6A | 2'x2' ARCHITECTURAL FLAT PANEL RECESSED TROFFER, LED, 5000 LUMEN, 4000K, 90 CRI, DIM TO 1% | PEERLESS LIGHTING | VMMRA G 90CRI 40K 5000LM DARK ZT 277 C110 | 51 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L6A
L7A | 4"x8' RECESSED HARD-LID LINEAR, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 MO R8 TMW BTW SC UNV X3 DM01 | 48 VA | 6 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7A
L7B | 4"x12' RECESSED LINEAR, LED, 1000 LUMEN PF, 4000K, DIM TO 1%, SEPARATELY CONTROLLED 6' SECTIONS | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 SO R12 TMW BTW SC UNV X1 DM01 | 96 VA | 8 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED | FIXTURE SHALL BE CONFIGURED SO THAT (2) 6' SECTIONS ARE INDEPENDENTLY CONTROLLED, IN A SINGLE SEAMLESS FIXTURE HOUSING | L7B
L7C | 4"x20' RECESSED LINEAR, LED, 1000 LUMEN PF, 4000K, DIM TO 1%, SEPARATELY CONTROLLED 10' SECTIONS | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 SO R20 TMW BTW SC UNV X1 DM01 | 160 VA | 8 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED | FIXTURE SHALL BE CONFIGURED SO THAT (2) 10' SECTIONS ARE INDEPENDENTLY CONTROLLED, IN A SINGLE SEAMLESS FIXTURE HOUSING | L7C
L7D | 4"x4' RECESSED LINEAR, LED, 1000 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 SO R4 TMW BTW SC UNV X1 DM01 | 32 VA | 8 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7D
L7E | 4"x4' RECESSED HARD-LID LINEAR, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 MO R4 TMW BTW SC UNV X3 DM01 | 24 VA | 6 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7E
L7G | 4"x6' RECESSED SPECIALTY CEILING HARD-LID LINEAR, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 MO R14 TMW BTW SC UNV X9 DM01 | 36 VA | 6 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7G
L7H | 4"x15' RECESSED SPECIALTY CEILING HARD-LID LINEAR, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 MO R23 TMW BTW SC UNV X9 DM01 | 90 VA | 6 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7H
L7J | 4"x11' RECESSED SPECIALTY CEILING HARD-LID LINEAR, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 MO R19 TMW BTW SC UNV X9 DM01 | 66 VA | 6 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7J
L7K | 4"x20' RECESSED SPECIALTY CEILING HARD-LID LINEAR, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 MO R28 TMW BTW SC UNV X9 DM01 | 120 VA | 6 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7K
L7L | 4"x3' RECESSED SPECIALTY CEILING HARD-LID LINEAR, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 MO R3 TMW BTW SC UNV X9 DM01 | 18 VA | 6 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7L
L7N | 4"x4' RECESSED LINEAR, LED, 1000 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 SO R4 TMW BTW SC UNV X1 DM01 | 40 VA | 8 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7N
L7NE | 4"x4' RECESSED LINEAR, LED, 1000 LUMEN PF, 4000K, DIM TO 1% WITH INTEGRAL EGRESS BATTERY UNIT | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 SO R4 TMW BTW SC UNV X1 DM01 EMHE | 40 VA | 8 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7NE
L7P | 4"x14' RECESSED LINEAR, LED, 1000 LUMEN PF, 4000K, DIM TO 1%, SEPARATELY CONTROLLED 6' SECTIONS | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 SO R12 TMW BTW SC UNV X1 DM01 | 112 VA | 8 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED | FIXTURE SHALL BE CONFIGURED SO THAT (2) 7' SECTIONS ARE INDEPENDENTLY CONTROLLED, IN A SINGLE SEAMLESS FIXTURE HOUSING | L7P
L7R | 4"x5' RECESSED HARD-LID LINEAR MUD-OVER FLANGE, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 SO R5 TMW BTW SC UNV X7 DM01 | 40 VA | 8 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7R
L8A | 2'x2' ARCHITECTURAL RECESSED TROFFER, LED, 3300 LUMEN, 4000K, DIM TO 1% | MARK ARCHITECTURAL LIGHTING | WHSPR LCTR 2X2 80CRI 40K 3300LM MIN1 277 SWC ZT | 30 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L8A
L9A | 4' STRIP, LED, 4000 LUMEN, 4000K | LITHONIA LIGHTING | CSS L48 MVOLT 40K 80CRI ZACVH | 35 VA |  | LED | FIXED OUTPUT | 277 V | PENDANT | MOUNT @ 10'-0" AFF TO BOTTOM OF FIXTURE | L9A
L10A | 4"x3' WALL MOUNTED LINEAR, LED, 675 LUMEN PF, 4000K | PRUDENTIAL LIGHTING | BIO-LIN LED4 MO R3 TMW AWL D1R NU SC UNV WS ND | 21 VA |  | LED | FIXED OUTPUT | 277 V | SURFACE, WALL | MOUNT @ 7'-0" AFF TO BOTTOM OF FIXTURE, CENTERED OVER MIRROR | L10A
L11A | 2'x4' FLAT PANEL RECESSED TROFFER, LED, 4800 LUMEN, 4000K, DIM TO 1% | LITHONIA LIGHTING | EPANL 2X4 4800LMHE 80CRI 40K MIN1 ZT MVOLT | 37 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L11A
L12A | 2"x24' RECESSED HARD LID LINEAR MUD-OVER FLANGE, LED, 390 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO2-REC LED4 LP R24 TMW SAL SC UNV X7 DM01 | 96 VA | 4 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L12A
L13A | 3' SURFACE MOUNTED LINEAR WITH ADJUSTABLE OPTIC, LED, 5596 LUMEN, 4000K, DIM TO 1% | ELLIPTIPAR | S 315 R03M S 00 M 0K 0 840 TD | 41 VA | 14 VA | LED | 1% 0-10V DIMMING | 277 V | SURFACE |  | L13A
L14A | RGBW COLOR CHANGING TAPE LIGHT, LED, 425 LUMEN PF, WITH ALUMINUM MOUNTING CHANNEL | KELVIX | RGBW 1 24V / CH-502-A 2 CL CP EC |  | 8 VA | LED | 1% 0-10V DIMMING | 277 V | SURFACE |  | L14A
L15A | 2'x2' FLAT PANEL RECESSED TROFFER, LED, 3400 LUMEN, 4000K, DIM TO 1% | LITHONIA LIGHTING | EPANL 2X2 3400LMHE 80CRI 40K MIN1 ZT MVOLT | 26 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L15A
L16A | 4" DIAMETER ROUND DOWNLIGHT, LED, 1500 LUMEN, 4000K, DIM TO 1% | GOTHAM LIGHTING | EVO4 40/1500 AR MWD LSS MVOLT GZ1 | 14 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L16A
L16AE | 4" DIAMETER ROUND DOWNLIGHT, LED, 1500 LUMEN, 4000K, DIM TO 1% WITH INTEGRAL EGRESS BATTERY UNIT | GOTHAM LIGHTING | EVO4 40/1500 AR MWD LSS MVOLT GZ1 EL | 14 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L16AE
L16B | 4" DIAMETER ROUND DOWNLIGHT, LED, 2500 LUMEN, 4000K, DIM TO 1% | GOTHAM LIGHTING | EVO4 40/2500 AR WD LSS MVOLT GZ1 | 26 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L16B
L16C | 4" DIAMETER ROUND DOWNLIGHT, LED, 2000 LUMEN, 4000K, DIM TO 1% | GOTHAM LIGHTING | EVO4 40/2000 AR WD LSS MVOLT GZ1 | 20 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L16C
L18A | 4"x22' LINEAR PENDANT, DIRECT/INDIRECT, LED, 843/281 LUMEN PF, 4000K, DIM TO 1% | FLUXWERX LIGHTING | APS R A C 40 B 22 G E1 M 03 | 187 VA | 9 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | MOUNT @ 10'-0" AFF TO BOTTOM OF FIXTURE | L18A
L19A | 26' MICRO WALL WASH, LED, 469 LUMEN PF, 4000K | PRUDENTIAL LIGHTING | MWR LED4 LO R26 TMW SC UNV WRM20" WRM1 TMW ND | 120 VA | 5 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | MOUNT @ 18" ABOVE TOP EDGE OF GRAPHIC TO BOTTOM OF FIXTURE | L19A
L20A | 5"x20' LINEAR PENDANT, DIRECT/INDIRECT, LED, 1025/575 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO5-LIN FLSH LED4 SO/LO R20 TMW BTW SCW ADC SC UNV CA48 DM01 | 240 VA | 12 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | BOTTOM OF FIXTURE SHALL BE FLUSH WITH BOTTOM OF DOUBLE T STRUCTURE | L20A
L20B | 5"x26' LINEAR PENDANT, DIRECT/INDIRECT, LED, 1025/575 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO5-LIN FLSH LED4 SO/LO R26 TMW BTW SCW ADC SC UNV CA48 DM01 | 312 VA | 12 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | BOTTOM OF FIXTURE SHALL BE FLUSH WITH BOTTOM OF DOUBLE T STRUCTURE | L20B
L20D | 5"x14' LINEAR PENDANT, DIRECT/INDIRECT, LED, 1025/575 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO5-LIN FLSH LED4 SO/LO R14 TMW BTW SCW ADC SC UNV CA48 DM01 | 168 VA | 12 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | BOTTOM OF FIXTURE SHALL BE FLUSH WITH BOTTOM OF DOUBLE T STRUCTURE | L20D
L20F | 5"x4' LINEAR PENDANT, DIRECT/INDIRECT, LED, 1025/575 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO5-LIN FLSH LED4 SO/LO R4 TMW BTW SCW ADC SC UNV CA48 DM01 | 48 VA | 12 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | BOTTOM OF FIXTURE SHALL BE FLUSH WITH BOTTOM OF DOUBLE T STRUCTURE | L20F
L20G | 5"x6' LINEAR PENDANT, DIRECT/INDIRECT, LED, 1025/575 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO5-LIN FLSH LED4 SO/LO R6 TMW BTW SCW ADC SC UNV CA48 DM01 | 72 VA | 12 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | BOTTOM OF FIXTURE SHALL BE FLUSH WITH BOTTOM OF DOUBLE T STRUCTURE | L20G
L20H | 5"x10' LINEAR PENDANT, DIRECT/INDIRECT, LED, 1025/575 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO5-LIN FLSH LED4 SO/LO R10 TMW BTW SCW ADC SC UNV CA48 DM01 | 120 VA | 12 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | BOTTOM OF FIXTURE SHALL BE FLUSH WITH BOTTOM OF DOUBLE T STRUCTURE | L20H
L20K | 5"x22' LINEAR PENDANT, DIRECT/INDIRECT, LED, 1025/575 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO5-LIN FLSH LED4 SO/LO R22 TMW BTW SCW ADC SC UNV CA48 DM01 | 264 VA | 12 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | BOTTOM OF FIXTURE SHALL BE FLUSH WITH BOTTOM OF DOUBLE T STRUCTURE | L20K
XA | EXIT SIGN, EDGE LIT, UNIVERSAL SURFACE MOUNT, GREEN LETTERING | SIGNTEX | CRS NB * G * BA * TW | 4 VA |  | LED | FIXED OUTPUT | 277 V | SURFACE | PROVIDE NUMBER OF FACES AND DIRECTIONAL ARROWS AS INDICATED ON PLANS; SINGLE-SIDED SIGNS SHALL HAVE CLEAR BACKGROUND, DOUBLE-SIDED FACES SHALL HAVE MIRRORED BACKGROUND | XA

## LIGHTING_FIXTURE_&_C_1
0 | 1 | 2 | 3 | 4 | 5
TIME BASED LIGHTING CONTROL SCHEDULE
LIGHTING CIRCUIT | LIGHTING ZONE | AREA | OPERATION | OVERRIDE TIMEOUT | COMMENTS
UCCSHA-1 U-INV-1 | b | LAB CORRIDORS | PROGRAM PER OWNER REQUIREMENTS | 2 HOURS
UCCHSA-5 U-INV-2 | h | ENTRY & STUDENT LIVING RM | PROGRAM PER OWNER REQUIREMENTS | 2 HOURS
UCCSHA-7 U-INV-2 | k | MAIN CIRCULATION EAST & CAFÉ | PROGRAM PER OWNER REQUIREMENTS | 2 HOURS
UCCSHA-7 | m | CAFÉ GRAPHIC ACCENT | PROGRAM PER OWNER REQUIREMENTS | NO OVERRIDE
UCCSHA-7 U-INV-2 | n | MAIN CIRCULATION INDIRECT | PROGRAM PER OWNER REQUIREMENTS | 2 HOURS
UCCSHA-9 | p | COVE ACCENT | PROGRAM PER OWNER REQUIREMENTS | NO OVERRIDE
UCCSHA-7 | r | MAIN CIRCULATION COLLABORATION | PROGRAM PER OWNER REQUIREMENTS | 2 HOURS
UCCSHA-7 U-INV-2 | s | MAIN CIRCULATION WEST | PROGRAM PER OWNER REQUIREMENTS | 2 HOURS
GENERAL NOTES 1) LOW VOLTAGE OVERRIDE SWITCHES SHOWN ON LIGHTING PLAN LABELED WITH LIGHTING ZONE SHALL OPERATE AS OVERRRIDE ON ONLY. OFF FUNCTION SHALL BE AUTOMATIC VIA PROGRAMMED TIME CONTROL DEVICE ONLY. 2) ALL LIGHTING ZONES EQUIPPED WITH OVERRIDE SWITCHES SHALL PROVIDE FLASH WARNING AT 15 AND 5 MINUTES PRIOR TO SWITCHING OFF. 3) A UL924 SWITCHING DEVICE IS REQIURED FOR ALL LIGHTING ZONES SERVED WITH NORMAL AND INVERTER BRANCH CIRCUITS. SEE LIGHTING PLAN GENERAL NOTES FOR ADDITIONAL INFORMATION.

## LIGHTING_FIXTURE_&_C_2
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
LIGHTING FIXTURE SCHEDULE
TYPE | DESCRIPTION | MANUFACTURER | MODEL | LOAD | WATTS PER FOOT (FOR CONTINUOUS RUNS) | LAMP | DRIVER | VOLTAGE | MOUNTING | COMMENTS | TYPE
L2A | 4"x22' LINEAR PENDANT, DIRECT/INDIRECT, LED, 810/910 LUMEN PF, 4000K, DIM TO 1% | PEERLESS LIGHTING | OPM4 LLP 22FT MSL8 80CRI 40K I910LMF 810LMF DARK ZT 277 DCT F1/ | 299 VA | 14 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | MOUNT @ 10'-0" AFF TO BOTTOM OF FIXTURE | L2A
L2B | 4"x16' LINEAR PENDANT, DIRECT/INDIRECT, LED, 810/910 LUMEN PF, 4000K, DIM TO 1% | PEERLESS LIGHTING | OPM4 LLP 16FT MSL8 80CRI 40K I910LMF 810LMF DARK ZT 277 DCT F1/ | 218 VA | 14 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | MOUNT @ 10'-0" AFF TO BOTTOM OF FIXTURE | L2B
L3A | 4" SQUARE DOWNLIGHT, LED, 1500 LUMEN, 4000K, DIM TO 1% | GOTHAM LIGHTING | EVO4SQ 40/15 AR LSS MVOLT GZ1 | 14 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L3A
L3B | 6" SQUARE DOWNLIGHT, LED, 2500 LUMEN, 4000K, DIM TO 1% | GOTHAM LIGHTING | EVO4SQ 40/25 AR LSS MVOLT GZ1 | 26 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L3B
L4A | 4" WIDE PERIMETER WALL-TO-WALL LINEAR RECESSED, ASSYMETRIC, LED, 875 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | P43-PSTD FLSH LED4 SO R(PER PLANS) TMW AWL D1R WTW SC X3B UNV DM01 |  | 10 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED | REFER TO LIGHTING PLANS FOR REQUIRED LENGTH | L4A
L4B | 4" WIDE PERIMETER WALL-TO-POCKET LINEAR RECESSED, ASSYMETRIC, LED, 875 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | P43-PSTD FLSH LED4 SO R(PER PLANS) TMW AWL D1R WTW/LP SC X3B UNV DM01 |  | 10 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED | REFER TO LIGHTING PLANS FOR REQUIRED LENGTH | L4B
L5A | 2'x4' ARCHITECTURAL RECESSED TROFFER, LED, 3000 LUMEN, 4000K, DIM TO 1% | MARK ARCHITECTURAL LIGHTING | WHSPR LCTR 2X4 80CRI 40K 3000LM MIN1 277 SWC ZT | 30 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L5A
L5B | 2'x4' ARCHITECTURAL RECESSED TROFFER, LED, 4000 LUMEN, 4000K, DIM TO 1% | MARK ARCHITECTURAL LIGHTING | WHSPR LCTR 2X4 80CRI 40K 4000LM MIN1 277 SWC ZT | 34 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L5B
L6A | 2'x2' ARCHITECTURAL FLAT PANEL RECESSED TROFFER, LED, 5000 LUMEN, 4000K, 90 CRI, DIM TO 1% | PEERLESS LIGHTING | VMMRA G 90CRI 40K 5000LM DARK ZT 277 C110 | 51 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L6A
L7A | 4"x8' RECESSED HARD-LID LINEAR, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 MO R8 TMW BTW SC UNV X3 DM01 | 48 VA | 6 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7A
L7B | 4"x12' RECESSED LINEAR, LED, 1000 LUMEN PF, 4000K, DIM TO 1%, SEPARATELY CONTROLLED 6' SECTIONS | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 SO R12 TMW BTW SC UNV X1 DM01 | 96 VA | 8 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED | FIXTURE SHALL BE CONFIGURED SO THAT (2) 6' SECTIONS ARE INDEPENDENTLY CONTROLLED, IN A SINGLE SEAMLESS FIXTURE HOUSING | L7B
L7C | 4"x20' RECESSED LINEAR, LED, 1000 LUMEN PF, 4000K, DIM TO 1%, SEPARATELY CONTROLLED 10' SECTIONS | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 SO R20 TMW BTW SC UNV X1 DM01 | 160 VA | 8 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED | FIXTURE SHALL BE CONFIGURED SO THAT (2) 10' SECTIONS ARE INDEPENDENTLY CONTROLLED, IN A SINGLE SEAMLESS FIXTURE HOUSING | L7C
L7D | 4"x4' RECESSED LINEAR, LED, 1000 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 SO R4 TMW BTW SC UNV X1 DM01 | 32 VA | 8 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7D
L7E | 4"x4' RECESSED HARD-LID LINEAR, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 MO R4 TMW BTW SC UNV X3 DM01 | 24 VA | 6 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7E
L7G | 4"x6' RECESSED SPECIALTY CEILING HARD-LID LINEAR, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 MO R14 TMW BTW SC UNV X9 DM01 | 36 VA | 6 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7G
L7H | 4"x15' RECESSED SPECIALTY CEILING HARD-LID LINEAR, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 MO R23 TMW BTW SC UNV X9 DM01 | 90 VA | 6 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7H
L7J | 4"x11' RECESSED SPECIALTY CEILING HARD-LID LINEAR, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 MO R19 TMW BTW SC UNV X9 DM01 | 66 VA | 6 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7J
L7K | 4"x20' RECESSED SPECIALTY CEILING HARD-LID LINEAR, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 MO R28 TMW BTW SC UNV X9 DM01 | 120 VA | 6 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7K
L7L | 4"x3' RECESSED SPECIALTY CEILING HARD-LID LINEAR, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 MO R3 TMW BTW SC UNV X9 DM01 | 18 VA | 6 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7L
L7N | 4"x4' RECESSED LINEAR, LED, 1000 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 SO R4 TMW BTW SC UNV X1 DM01 | 40 VA | 8 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7N
L7NE | 4"x4' RECESSED LINEAR, LED, 1000 LUMEN PF, 4000K, DIM TO 1% WITH INTEGRAL EGRESS BATTERY UNIT | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 SO R4 TMW BTW SC UNV X1 DM01 EMHE | 40 VA | 8 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7NE
L7P | 4"x14' RECESSED LINEAR, LED, 1000 LUMEN PF, 4000K, DIM TO 1%, SEPARATELY CONTROLLED 6' SECTIONS | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 SO R12 TMW BTW SC UNV X1 DM01 | 112 VA | 8 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED | FIXTURE SHALL BE CONFIGURED SO THAT (2) 7' SECTIONS ARE INDEPENDENTLY CONTROLLED, IN A SINGLE SEAMLESS FIXTURE HOUSING | L7P
L7R | 4"x5' RECESSED HARD-LID LINEAR MUD-OVER FLANGE, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 SO R5 TMW BTW SC UNV X7 DM01 | 40 VA | 8 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L7R
L8A | 2'x2' ARCHITECTURAL RECESSED TROFFER, LED, 3300 LUMEN, 4000K, DIM TO 1% | MARK ARCHITECTURAL LIGHTING | WHSPR LCTR 2X2 80CRI 40K 3300LM MIN1 277 SWC ZT | 30 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L8A
L9A | 4' STRIP, LED, 4000 LUMEN, 4000K | LITHONIA LIGHTING | CSS L48 MVOLT 40K 80CRI ZACVH | 35 VA |  | LED | FIXED OUTPUT | 277 V | PENDANT | MOUNT @ 10'-0" AFF TO BOTTOM OF FIXTURE | L9A
L10A | 4"x3' WALL MOUNTED LINEAR, LED, 675 LUMEN PF, 4000K | PRUDENTIAL LIGHTING | BIO-LIN LED4 MO R3 TMW AWL D1R NU SC UNV WS ND | 21 VA |  | LED | FIXED OUTPUT | 277 V | SURFACE, WALL | MOUNT @ 7'-0" AFF TO BOTTOM OF FIXTURE, CENTERED OVER MIRROR | L10A
L11A | 2'x4' FLAT PANEL RECESSED TROFFER, LED, 4800 LUMEN, 4000K, DIM TO 1% | LITHONIA LIGHTING | EPANL 2X4 4800LMHE 80CRI 40K MIN1 ZT MVOLT | 37 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L11A
L12A | 2"x24' RECESSED HARD LID LINEAR MUD-OVER FLANGE, LED, 390 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO2-REC LED4 LP R24 TMW SAL SC UNV X7 DM01 | 96 VA | 4 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L12A
L13A | 3' SURFACE MOUNTED LINEAR WITH ADJUSTABLE OPTIC, LED, 5596 LUMEN, 4000K, DIM TO 1% | ELLIPTIPAR | S 315 R03M S 00 M 0K 0 840 TD | 41 VA | 14 VA | LED | 1% 0-10V DIMMING | 277 V | SURFACE |  | L13A
L14A | RGBW COLOR CHANGING TAPE LIGHT, LED, 425 LUMEN PF, WITH ALUMINUM MOUNTING CHANNEL | KELVIX | RGBW 1 24V / CH-502-A 2 CL CP EC |  | 8 VA | LED | 1% 0-10V DIMMING | 277 V | SURFACE |  | L14A
L15A | 2'x2' FLAT PANEL RECESSED TROFFER, LED, 3400 LUMEN, 4000K, DIM TO 1% | LITHONIA LIGHTING | EPANL 2X2 3400LMHE 80CRI 40K MIN1 ZT MVOLT | 26 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L15A
L16A | 4" DIAMETER ROUND DOWNLIGHT, LED, 1500 LUMEN, 4000K, DIM TO 1% | GOTHAM LIGHTING | EVO4 40/1500 AR MWD LSS MVOLT GZ1 | 14 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L16A
L16AE | 4" DIAMETER ROUND DOWNLIGHT, LED, 1500 LUMEN, 4000K, DIM TO 1% WITH INTEGRAL EGRESS BATTERY UNIT | GOTHAM LIGHTING | EVO4 40/1500 AR MWD LSS MVOLT GZ1 EL | 14 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L16AE
L16B | 4" DIAMETER ROUND DOWNLIGHT, LED, 2500 LUMEN, 4000K, DIM TO 1% | GOTHAM LIGHTING | EVO4 40/2500 AR WD LSS MVOLT GZ1 | 26 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L16B
L16C | 4" DIAMETER ROUND DOWNLIGHT, LED, 2000 LUMEN, 4000K, DIM TO 1% | GOTHAM LIGHTING | EVO4 40/2000 AR WD LSS MVOLT GZ1 | 20 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED |  | L16C
L18A | 4"x22' LINEAR PENDANT, DIRECT/INDIRECT, LED, 843/281 LUMEN PF, 4000K, DIM TO 1% | FLUXWERX LIGHTING | APS R A C 40 B 22 G E1 M 03 | 187 VA | 9 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | MOUNT @ 10'-0" AFF TO BOTTOM OF FIXTURE | L18A
L19A | 26' MICRO WALL WASH, LED, 469 LUMEN PF, 4000K | PRUDENTIAL LIGHTING | MWR LED4 LO R26 TMW SC UNV WRM20" WRM1 TMW ND | 120 VA | 5 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | MOUNT @ 18" ABOVE TOP EDGE OF GRAPHIC TO BOTTOM OF FIXTURE | L19A
L20A | 5"x20' LINEAR PENDANT, DIRECT/INDIRECT, LED, 1025/575 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO5-LIN FLSH LED4 SO/LO R20 TMW BTW SCW ADC SC UNV CA48 DM01 | 240 VA | 12 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | BOTTOM OF FIXTURE SHALL BE FLUSH WITH BOTTOM OF DOUBLE T STRUCTURE | L20A
L20B | 5"x26' LINEAR PENDANT, DIRECT/INDIRECT, LED, 1025/575 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO5-LIN FLSH LED4 SO/LO R26 TMW BTW SCW ADC SC UNV CA48 DM01 | 312 VA | 12 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | BOTTOM OF FIXTURE SHALL BE FLUSH WITH BOTTOM OF DOUBLE T STRUCTURE | L20B
L20D | 5"x14' LINEAR PENDANT, DIRECT/INDIRECT, LED, 1025/575 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO5-LIN FLSH LED4 SO/LO R14 TMW BTW SCW ADC SC UNV CA48 DM01 | 168 VA | 12 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | BOTTOM OF FIXTURE SHALL BE FLUSH WITH BOTTOM OF DOUBLE T STRUCTURE | L20D
L20F | 5"x4' LINEAR PENDANT, DIRECT/INDIRECT, LED, 1025/575 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO5-LIN FLSH LED4 SO/LO R4 TMW BTW SCW ADC SC UNV CA48 DM01 | 48 VA | 12 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | BOTTOM OF FIXTURE SHALL BE FLUSH WITH BOTTOM OF DOUBLE T STRUCTURE | L20F
L20G | 5"x6' LINEAR PENDANT, DIRECT/INDIRECT, LED, 1025/575 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO5-LIN FLSH LED4 SO/LO R6 TMW BTW SCW ADC SC UNV CA48 DM01 | 72 VA | 12 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | BOTTOM OF FIXTURE SHALL BE FLUSH WITH BOTTOM OF DOUBLE T STRUCTURE | L20G
L20H | 5"x10' LINEAR PENDANT, DIRECT/INDIRECT, LED, 1025/575 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO5-LIN FLSH LED4 SO/LO R10 TMW BTW SCW ADC SC UNV CA48 DM01 | 120 VA | 12 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | BOTTOM OF FIXTURE SHALL BE FLUSH WITH BOTTOM OF DOUBLE T STRUCTURE | L20H
L20K | 5"x22' LINEAR PENDANT, DIRECT/INDIRECT, LED, 1025/575 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO5-LIN FLSH LED4 SO/LO R22 TMW BTW SCW ADC SC UNV CA48 DM01 | 264 VA | 12 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | BOTTOM OF FIXTURE SHALL BE FLUSH WITH BOTTOM OF DOUBLE T STRUCTURE | L20K
XA | EXIT SIGN, EDGE LIT, UNIVERSAL SURFACE MOUNT, GREEN LETTERING | SIGNTEX | CRS NB * G * BA * TW | 4 VA |  | LED | FIXED OUTPUT | 277 V | SURFACE | PROVIDE NUMBER OF FACES AND DIRECTIONAL ARROWS AS INDICATED ON PLANS; SINGLE-SIDED SIGNS SHALL HAVE CLEAR BACKGROUND, DOUBLE-SIDED FACES SHALL HAVE MIRRORED BACKGROUND | XA

## ELECTRICAL_PANELBOAR_0
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Lighting Inverter: U-INV Location: ELEC. N140 Volts: 277 A.I.C. Rating: 65,000 Supply From: UCCSHA Phases: 1 Mains Type: MCB Mounting: FLOOR Wires: 2 Mains Rating: Enclosure: MCB Rating: 20 A
CKT | Circuit Description | Trip | Poles | # of Poles | Frame Size | Trip Rating |  | Load | Remarks | Poles | Trip | Circuit Description |  | CKT
1 | LTG EMERGENCY EGRESS UCCS NORTH | 20 A | 1 | 1 | 20 A | 20 A |  | 1294 VA |  | 1 | 20 A | RCPT STUDENT LIVING ROOM N102 |  | 2
2 | LTG EMERGENCY EGRESS UCCS SOUTH | 20 A | 1 | 1 | 20 A | 20 A | 720 | 2388 VA |  | 1 | 20 A | RCPT STUDENT LIVING RM N101, VSTBL N102 |  | 4
3 | SPARE | 20 A | 1 | 1 | -- | 20 A |  | 0 VA | 750 | 1 | 20 A | RCPT WALL MONITORS CIRCULATION N119 E |  | 6
4 | NON USABLE SPACE | 20 A | 1 | -- | -- | -- |  | 0 VA | -- | 1 | 20 A | RECEPTACLE ROOM N119, E-197 |  | 8
5 | NON USABLE SPACE | 20 A | 1 | -- | -- | -- | 1000 | 0 VA | -- | 1 | 20 A | RCPT AV CAB EXECUTIVE CONFERENCE N1... |  | 10
6 | NON USABLE SPACE | 20 A | 1 | -- | -- | -- |  | 0 VA | -- | 1 | 20 A | RCPT AV CAB EXECUTIVE CONFERENCE N1... |  | 12
7 | NON USABLE SPACE | 20 A | 1 | -- | -- | -- |  | 0 VA | -- | 1 | 20 A | RCPT LECTERN EXECUTIVE CONFERENCE... |  | 14
8 | NON USABLE SPACE | 20 A | 1 | -- | -- | -- | 0 | 0 VA | -- | 1 | 20 A | SPARE |  | 16
9 | NON USABLE SPACE | 20 A | 1 | -- | -- | -- |  | 0 VA | -- | 1 | 20 A | SPARE |  | 18
10 | NON USABLE SPACE | 20 A | 1 | -- | -- | -- |  | 0 VA | -- | 1 | 20 A | SPARE |  | 20
11 | NON USABLE SPACE | 20 A | 1 | -- | -- | -- | 0 | 0 VA | -- | 1 | 20 A | SPARE |  | 22
12 | NON USABLE SPACE | 20 A | 1 | -- | -- | -- |  | 0 VA | -- | 1 | 20 A | SPARE |  | 24
13 | NON USABLE SPACE | 20 A | 1 | -- | -- | -- |  | 0 VA | -- | 1 | 20 A | SPARE |  | 26
14 | NON USABLE SPACE | 20 A | 1 | -- | -- | -- | 0 | 0 VA | -- | -- | -- | SPACE |  | 28
Total Conn. Load: 3682 VA Total Amps: 13 A | RCPT PROJECTOR EXECUTIVE CONF N105 | 20 A | 1 |  |  |  |  | 3682 VA | 0 | -- | -- | SPACE |  | 30
Load Classification | PROJECTION SCREEN EXECUTIVE CONF N105 | Connected Load | Demand Factor | 600 | Estimated Demand |  | Panel Totals |  |  | -- | -- | SPACE |  | 32
Lighting | RCPT CNTR TOP EXECUTIVE CONF N105 | 3682 VA | 125.00% |  | 4602 VA | 360 | 0 |  |  | -- | -- | SPACE |  | 34
35 | RCPT CNTR TOP EXECUTIVE CONF N105 | 20 A | 1 |  |  |  | Total Conn. Load: | 360 | 0 | 3682 VA | -- | SPACE |  | 36
37 | RCPT OFFICE N104B, N104C | 20 A | 1 | 1480 | 0 |  | Total Est. Demand: |  |  | 4602 VA | -- | SPACE |  | 38
39 | RCPT OFFICE N104A, N104D | 20 A | 1 |  |  | 1300 | Total Conn.: |  |  | 13 A | -- | SPACE |  | 40
41 | RCPT OFFICE N104E, N104F | 20 A | 1 |  |  |  | Total Est. Demand: | 1120 | 0 | 17 A | -- | SPACE |  | 42
Total Load: 20744 VA 20582 VA 19236 VA Total Amps: 175 A 173 A 160 A |  |  |  | 20744 VA |  | 20582 VA |  | 19236 VA
Load Classification |  | Connected Load |  |  | Demand Factor |  |  | Estimated Demand |  |  | Panel Totals
Notes: MYERS ILLUMINATOR SUPERNOVA 3.75kVA EMERGENCY LIGHTING INVERTER, OR EQUAL. |  | 18560 VA |  |  | 76.94% |  |  | 14280 VA
Power |  | 26460 VA |  |  | 100.00% |  |  | 26460 VA |  |  | Total Conn. Load: |  | 60562 VA
Mechanical Equipment |  | 15542 VA |  |  | 106.69% |  |  | 16582 VA |  |  | Total Est. Demand: |  | 57322 VA
[11 empty] | Total Conn.: |  | 168 A
[11 empty] | Total Est. Demand: |  | 159 A
Notes:

## ELECTRICAL_PANELBOAR_1
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Lighting Inverter: I-INV Location: ELEC. S105 Volts: 277 A.I.C. Rating: 65,000 Supply From: ISACHA Phases: 1 Mains Type: MCB Mounting: WALL Wires: 2 Mains Rating: Enclosure: MCB Rating: 20 A
CKT | Circuit Description | Trip | Poles | # of Poles | Frame Size | Trip Rating |  | Load | Remarks | Poles | Trip | Circuit Description |  | CKT
1 | LTG EMERGENCY EGRESS SPACE ISAC | 20 A | 1 | 1 | 20 A | 20 A |  | 807 VA |  | 1 | 20 A | EMERGENCY LIGHTING INVERTER U-INV |  | 2
2 | SPARE | 20 A | 1 | 1 | -- | 20 A | 0 | 0 VA |  | 1 | 20 A | SPARE |  | 4
3 | NON USABLE SPACE | 20 A | 1 | -- | -- | -- |  | 0 VA | -- | 1 | 20 A | SPARE |  | 6
4 | NON USABLE SPACE | 20 A | 1 | -- | -- | -- |  | 0 VA | -- | 1 | 20 A | SPARE |  | 8
5 | NON USABLE SPACE | 20 A | 1 | -- | -- | -- | 0 | 0 VA | -- | 1 | 20 A | SPARE |  | 10
6 | NON USABLE SPACE | -- | -- | -- | -- | -- |  | 0 VA | -- | -- | -- | SPACE |  | 12
7 | NON USABLE SPACE | -- | -- | -- | -- | -- |  | 0 VA | -- | -- | -- | SPACE |  | 14
8 | NON USABLE SPACE | -- | -- | -- | -- | -- | 0 | 0 VA | -- | -- | -- | SPACE |  | 16
9 | NON USABLE SPACE | -- | -- | -- | -- | -- |  | 0 VA | -- | -- | -- | SPACE |  | 18
10 | NON USABLE SPACE | -- | -- | -- | -- | -- |  | 0 VA | -- | -- | -- | SPACE |  | 20
11 | NON USABLE SPACE | -- | -- | -- | -- | -- | 0 | 0 VA | -- | -- | -- | SPACE |  | 22
12 | NON USABLE SPACE | -- | -- | -- | -- | -- |  | 0 VA | -- | -- | -- | SPACE |  | 24
13 | NON USABLE SPACE | -- | -- | -- | -- | -- |  | 0 VA | -- | -- | -- | SPACE |  | 26
14 | NON USABLE SPACE | -- | -- | -- | -- | -- | 0 | 0 VA | -- | -- | -- | SPACE |  | 28
Total Conn. Load: 807 VA Total Amps: 3 A | SPACE | -- | -- |  |  |  |  | 807 VA | 0 | -- | -- | SPACE |  | 30
Load Classification | SPACE | Connected Load | Demand Factor | 0 | Estimated Demand |  | Panel Totals |  |  | -- | -- | SPACE |  | 32
Lighting | SPACE | 807 VA | 125.00% |  | 1008 VA | 0 | 0 |  |  | -- | -- | SPACE |  | 34
35 | SPACE | -- | -- |  |  |  | Total Conn. Load: | 0 | 0 | 807 VA | -- | SPACE |  | 36
37 | T-UCCS-LA/LC | 225 A | 3 | 41474 | 1860 |  | Total Est. Demand: |  |  | 1008 VA | 50 A | T-UCCS-SA |  | 38
39 | [5 empty] | 44482 | Total Conn.: |  |  | 3 A |  |  |  | 40
41 | [6 empty] | Total Est. Demand: | 40866 | 2500 | 4 A |  |  |  | 42
Total Load: 50948 VA 50957 VA 45762 VA Total Amps: 187 A 187 A 165 A |  |  |  | 50948 VA |  | 50957 VA |  | 45762 VA
Load Classification |  | Connected Load |  |  | Demand Factor |  |  | Estimated Demand |  |  | Panel Totals
Notes: MYERS ILLUMINATOR EM 1.6kVA EMERGENCY LIGHTING INVERTER, OR EQUAL. |  | 14625 VA |  |  | 125.00% |  |  | 18282 VA
Power |  | 85060 VA |  |  | 100.00% |  |  | 85060 VA |  |  | Total Conn. Load: |  | 147667 VA
Receptacle |  | 32440 VA |  |  | 65.41% |  |  | 21220 VA |  |  | Total Est. Demand: |  | 141144 VA
Mechanical Equipment |  | 15542 VA |  |  | 106.69% |  |  | 16582 VA |  |  | Total Conn.: |  | 178 A
[11 empty] | Total Est. Demand: |  | 170 A
Notes:

## ELECTRICAL_PANELBOAR_2
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Panelboard: ISACHA Location: ELEC. S105 Volts: 480Y/277 A.I.C. Rating: REFER TO FAULT CALCULATIONS Supply From: MSB-SOUTH Phases: 3 Mains Type: MLO Mounting: Surface Wires: 4 Bus Rating: 400 A Enclosure: Type 1
CKT | Circuit Description | Trip | Poles | A (VA) |  | B (VA) |  | C (VA) |  | Poles | Trip | Circuit Description |  | CKT
1 | LTG ISAC SOUTH | 20 A | 1 | 1333 | 807 |  |  |  |  | 1 | 20 A | EMERGENCY LTG INVERTER I-INV |  | 2
3 | LTG ISAC NORTH | 20 A | 1 |  |  | 858 | 0 |  |  | 1 | 20 A | SPARE |  | 4
5 | SPACE | -- | -- |  |  |  |  | 0 | 0 | 1 | 20 A | SPARE |  | 6
7 | SPACE | -- | -- | 0 | 0 |  |  |  |  | 1 | 20 A | SPARE |  | 8
9 | SPACE | -- | -- |  |  | 0 | 0 |  |  | 1 | 20 A | SPARE |  | 10
11 | SPACE | -- | -- |  |  |  |  | 0 | 0 | -- | -- | SPACE |  | 12
13 | SPACE | -- | -- | 0 | 0 |  |  |  |  | -- | -- | SPACE |  | 14
15 | SPACE | -- | -- |  |  | 0 | 0 |  |  | -- | -- | SPACE |  | 16
17 | SPACE | -- | -- |  |  |  |  | 0 | 0 | -- | -- | SPACE |  | 18
19 | SPACE | -- | -- | 0 | 0 |  |  |  |  | -- | -- | SPACE |  | 20
21 | SPACE | -- | -- |  |  | 0 | 0 |  |  | -- | -- | SPACE |  | 22
23 | WH-1 | 70 A | 1 |  |  |  |  | 16066 | 0 | -- | -- | SPACE |  | 24
25 | A) CRAC-1 DATA/SERVER S103 | 70 A | 3 | 7908 | 388 |  |  |  |  | 3 | 20 A | A) CU-4 |  | 26
27 | SPACE | -- | -- |  |  | 7908 | 388 |  |  | -- | -- | SPACE |  | 28
29 | SPACE | -- | -- |  |  |  |  | 7908 | 388 | -- | -- | SPACE |  | 30
31 | A) CRAC-2 DATA/SERVER S103 | 70 A | 3 | 7908 | 388 | 1860 VA |  | 2500 VA |  | 3 | 20 A | A) CU-5 |  | 32
33 |  | Connected Load |  |  | Demand Factor | 7908 | 388 | Estimated Demand |  |  | Panel Totals |  |  | 34
35 |  | 720 VA |  |  | 100.00% |  |  | 7908 | 388 |  |  |  |  | 36
37 | T-ISAC-LA/WA | 110 A | 3 | 13340 | 14140 |  |  | 5500 VA |  | 3 | 110 A | T-ISAC-SA | 6220 VA | 38
39 | [5 empty] | 13050 | 15720 |  |  |  | Total Est. Demand: |  | 6220 VA | 40
41 | [7 empty] | 12090 | 14140 |  | Total Conn.: |  | 17 A | 42
Total Load: 46212 VA 46220 VA 58888 VA Total Amps: 167 A 167 A 213 A |  |  |  | 46212 VA |  | 46220 VA |  | 58888 VA |  |  | Total Est. Demand: |  | 17 A
Load Classification |  | Connected Load |  |  | Demand Factor |  |  | Estimated Demand |  |  | Panel Totals
Lighting |  | 2997 VA |  |  | 125.00% |  |  | 3746 VA
Power |  | 79796 VA |  |  | 100.00% |  |  | 79796 VA |  |  | Total Conn. Load: |  | 151320 VA
Receptacle |  | 18000 VA |  |  | 77.78% |  |  | 14000 VA |  |  | Total Est. Demand: |  | 154000 VA
Mechanical Equipment |  | 50527 VA |  |  | 111.74% |  |  | 56458 VA |  |  | Total Conn.: |  | 182 A
[11 empty] | Total Est. Demand: |  | 185 A
Notes: A) CRAC-1 / 2 AND CU-4 / 5 ARE NON SIMULTANEOUS LOADS. EACH PAIR OF NON SIMULATANEOUS UNITS ARE SHOWN AT 50% OF EQUIPMENT LOAD FOR CALCULATION PURPOSES.

## ELECTRICAL_PANELBOAR_3
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Branch Panel: ISACSA Location: DATA/SERVER S103 Volts: 208Y/120 A.I.C. Rating: REFER TO FAULT CALCULATIONS Supply From: T-ISAC-SA Phases: 3 Mains Type: MCB Mounting: Surface Wires: 4 Mains Rating: 200 A Enclosure: Type 1 MCB Rating: 200 A
CKT | Circuit Description | Trip | Poles | A |  | B |  | C |  | Poles | Trip | Circuit Description |  | CKT
1 | RCPT DATA/SERVER S103 S, W | 20 A | 1 | 540 | 0 |  |  |  |  | 1 | 20 A | SPARE |  | 2
3 | RCPT DATA/SERVER S103 W, N | 20 A | 1 |  |  | 540 | 0 |  |  | 1 | 20 A | SPARE |  | 4
5 | SECURITY CABINET DATA/SERVER S103 | 20 A | 1 |  |  |  |  | 1000 | 0 | 1 | 20 A | SPARE |  | 6
7 | RCPT DATA/SERVER S103 ROW 1 | 30 A | 2 | 1040 | 1040 |  |  |  |  | 2 | 30 A | RCPT DATA/SERVER S103 ROW 1 |  | 8
9 | RCPT SMALL CONFERENCE N120C | 20 A | 1 |  |  | 1040 | 1040 |  |  | 1 | 20 A | RCPT AV CAB EXECUTIVE CONFERENCE N1... |  | 10
11 | RCPT DATA/SERVER S103 ROW 1 | 30 A | 2 |  |  |  |  | 1040 | 1040 | 2 | 30 A | RCPT DATA/SERVER S103 ROW 2 |  | 12
13 | RCPT CORRIDOR N119, CIRCULATION N120 | 20 A | 1 | 1040 | 1040 |  |  |  |  | 1 | 20 A | RCPT LECTERN EXECUTIVE CONFERENCE... |  | 14
15 | RCPT DATA/SERVER S103 ROW 1 | 30 A | 2 |  |  | 1040 | 1040 |  |  | 2 | 30 A | RCPT DATA/SERVER S103 ROW 2 |  | 16
17 | RCPT COPIER COPY OFFICE SUPPLIES N120B | 20 A | 1 |  |  |  |  | 1040 | 1040 | 1 | 20 A | SPARE |  | 18
19 | RCPT DATA/SERVER S103 ROW 1 | 30 A | 2 | 1040 | 1040 |  |  |  |  | 2 | 30 A | RCPT DATA/SERVER S103 ROW 2 |  | 20
21 | RCPT S EXECUTIVE CONFERENCE N105 | 20 A | 1 |  |  | 1040 | 1040 |  |  | 1 | 20 A | SPARE |  | 22
23 | RCPT DATA/SERVER S103 ROW 1 | 30 A | 2 |  |  |  |  | 1040 | 1040 | 2 | 30 A | RCPT DATA/SERVER S103 ROW 2 |  | 24
25 | RCPT FLR BOX EXECUTIVE CONFERENCE... | 20 A | 1 | 1040 | 1040 |  |  |  |  | 1 | 20 A | SPARE |  | 26
27 | RCPT DATA/SERVER S103 ROW 1 | 30 A | 2 |  |  | 1040 | 1040 |  |  | 2 | 30 A | RCPT DATA/SERVER S103 ROW 2 |  | 28
29 | RCPT PROJECTOR EXECUTIVE CONF N105 | 20 A | 1 |  |  |  |  | 1040 | 1040 | -- | -- | SPACE |  | 30
31 | RCPT DATA/SERVER S103 ROW 1 | 30 A | 2 | 1040 | 1040 |  |  |  |  | 2 | 30 A | RCPT DATA/SERVER S103 ROW 2 |  | 32
33 | RCPT CNTR TOP EXECUTIVE CONF N105 | 20 A | 1 |  |  | 1040 | 1040 |  |  | -- | -- | SPACE |  | 34
35 | RCPT DATA/SERVER S103 ROW 2 | 20 A | 1 |  |  |  |  | 1600 | 1600 | 1 | 20 A | RCPT DATA/SERVER S103 ROW 2 |  | 36
37 | RCPT DATA/SERVER S103 ROW 2 | 20 A | 1 | 1600 | 1600 |  |  |  |  | 1 | 20 A | RCPT DATA/SERVER S103 ROW 2 |  | 38
39 | RCPT DATA/SERVER S103 ROW 2 | 20 A | 1 |  |  | 1600 | 1600 |  |  | 1 | 20 A | RCPT DATA/SERVER S103 ROW 2 |  | 40
41 | RCPT DATA/SERVER S103 ROW 2 | 20 A | 1 |  |  |  |  | 1600 | 1600 | 1 | 20 A | RCPT DATA/SERVER S103 ROW 2 |  | 42
43 | SPARE | 20 A | 1 | 0 | 0 | 20582 VA |  | 19236 VA |  | 1 | 20 A | SPARE |  | 44
45 | SPACE | -- | -- |  | Demand Factor | 0 | 0 | Estimated Demand |  | -- | -- | SPACE |  | 46
47 | SPACE | -- | -- |  | 76.94% |  |  | 0 | 0 | -- | -- | SPACE |  | 48
49 | SPACE | -- | -- | 0 | 0 |  |  | 26460 VA |  | -- | -- | SPACE | 60562 VA | 50
51 | SPACE | -- | -- |  | 106.69% | 0 | 0 | 16582 VA |  | -- | -- | SPACE | 57322 VA | 52
53 | SPACE | -- | -- |  |  |  |  | 0 | 0 | -- | -- | SPACE | 168 A | 54
Total Load: 14140 VA 14140 VA 15720 VA Total Amps: 118 A 118 A 131 A |  |  |  | 14140 VA |  | 14140 VA |  | 15720 VA |  |  | Total Est. Demand: |  | 159 A
Load Classification |  | Connected Load |  |  | Demand Factor |  |  | Estimated Demand |  |  | Panel Totals
Receptacle |  | 1080 VA |  |  | 100.00% |  |  | 1080 VA
Power |  | 42920 VA |  |  | 100.00% |  |  | 42920 VA |  |  | Total Conn. Load: |  | 44000 VA
[11 empty] | Total Est. Demand: |  | 44000 VA
[11 empty] | Total Conn.: |  | 122 A
[11 empty] | Total Est. Demand: |  | 122 A
Notes:

## ELECTRICAL_PANELBOAR_4
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Branch Panel: ISACWA Location: ELEC. S105 Volts: 208Y/120 A.I.C. Rating: REFER TO FAULT CALCULATIONS Supply From: T-ISAC-LA/WA Phases: 3 Mains Type: MCB/FTL Mounting: Surface Wires: 4 Mains Rating: 125 A Enclosure: Type 1 MCB Rating: 125 A
CKT | Circuit Description | Trip | Poles | A (VA) |  | B (VA) |  | C (VA) |  | Poles | Trip | Circuit Description |  | CKT
1 | SYSTEMS FURNITURE WATCH CENTER S107 | 20 A | 2 | 800 | 540 |  |  |  |  | 1 | 20 A | RCPT CVL VESTIBULE S102A |  | 2
3 | RCPT WORKSTATIONS GRAD LAB MEDIUM... | 20 A | 1 |  |  | 800 | 610 |  |  | 1 | 20 A | RCPT CYBER VULNERABILITY LAB S102 N |  | 4
5 | SYSTEMS FURNITURE WATCH CENTER S107 | 20 A | 2 |  |  |  |  | 800 | 1200 | 1 | 20 A | RCPT SERVER CABINET CVL S102 S |  | 6
7 | RCPT GRAD LAB MEDIUM N118 | 20 A | 1 | 800 | 1040 |  |  |  |  | 2 | 30 A | RCPT SERVER CABINET CVL S102 S |  | 8
9 | SYSTEMS FURNITURE WATCH CENTER S107 | 20 A | 2 |  |  | 800 | 1040 |  |  | 1 | 20 A | RCPT WORKSTATIONS GRAD LAB LARGE N110 |  | 10
11 | RCPT WORKSTATIONS GRAD LAB MEDIUM... | 20 A | 1 |  |  |  |  | 800 | 1200 | 1 | 20 A | RCPT SERVER CABINET CVL S102 N |  | 12
13 | SYSTEMS FURNITURE WATCH CENTER S107 | 20 A | 2 | 800 | 1040 |  |  |  |  | 2 | 30 A | RCPT SERVER CABINET CVL S102 N |  | 14
15 | RCPT GRAD LAB MEDIUM N117 | 20 A | 1 |  |  | 800 | 1040 |  |  | 1 | 20 A | RCPT GRAD LAB LARGE N110 |  | 16
17 | SYSTEMS FURNITURE WATCH CENTER S107 | 20 A | 2 |  |  |  |  | 800 | 1080 | 1 | 20 A | RCPT RACEWAY CVL S102 S |  | 18
19 | RCPT WORKSTATIONS GRAD LAB MEDIUM... | 20 A | 1 | 800 | 1080 |  |  |  |  | 1 | 20 A | RCPT RACEWAY CVL S102 S |  | 20
21 | SYSTEMS FURNITURE WATCH CENTER S107 | 20 A | 2 |  |  | 800 | 1080 |  |  | 1 | 20 A | RCPT RACEWAY CVL S102 S |  | 22
23 | GRAD LAB MEDIUM N116 | 20 A | 1 |  |  |  |  | 800 | 1080 | 1 | 20 A | RCPT RACEWAY CVL S102 N |  | 24
25 | RCPT FLOOR BOX WATCH CENTER S107 | 20 A | 1 | 500 | 1080 |  |  |  |  | 1 | 20 A | RCPT RACEWAY CVL S102 N |  | 26
27 | RCPT FLOOR BOX WATCH CENTER S107 | 20 A | 1 |  |  | 500 | 1080 |  |  | 1 | 20 A | RCPT RACEWAY CVL S102 N |  | 28
29 | RCPT FLOOR BOX WATCH CENTER S107 | 20 A | 1 |  |  |  |  | 500 | 1440 | 1 | 20 A | RCPT RACEWAY CVL S102 E |  | 30
31 | RECEPTACLE WATCH CENTER S107 | 20 A | 1 | 720 | 1440 |  |  |  |  | 1 | 20 A | RCPT RACEWAY CVL S102 E |  | 32
33 | RECEPTACLE WATCH CENTER S107 | 20 A | 1 |  |  | 900 | 0 |  |  | 1 | 20 A | SPARE |  | 34
35 | SPARE | 20 A | 1 |  |  |  |  | 0 | 0 | 1 | 20 A | SPARE |  | 36
37 | SPARE | 20 A | 1 | 0 | 0 |  |  |  |  | -- | -- | SPACE |  | 38
39 | CU-4, 5 CONTROL | 20 A | 1 |  |  | 300 | 0 |  |  | -- | -- | SPACE |  | 40
41 | CRAC-1, 2 CONTROL | 20 A | 1 |  |  |  |  | 300 | 0 | -- | -- | SPACE |  | 42
Total Load: 10640 VA 9750 VA 10000 VA Total Amps: 89 A 81 A 84 A |  |  |  | 10640 VA |  | 9750 VA |  | 10000 VA
Load Classification |  | Connected Load |  |  | Demand Factor |  |  | Estimated Demand |  |  | Panel Totals
Receptacle |  | 11880 VA |  |  | 92.09% |  |  | 10940 VA
Power |  | 18510 VA |  |  | 100.00% |  |  | 18510 VA |  |  | Total Conn. Load: |  | 30390 VA
[11 empty] | Total Est. Demand: |  | 29450 VA
[11 empty] | Total Conn.: |  | 84 A
[11 empty] | Total Est. Demand: |  | 82 A
Notes:

## ELECTRICAL_PANELBOAR_5
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Branch Panel: ISACLA Location: ELEC. S105 Volts: 208Y/120 A.I.C. Rating: REFER TO FAULT CALCULATIONS Supply From: T-ISAC-LA/WA Phases: 3 Mains Type: MCB Mounting: Surface Wires: 4 Mains Rating: 125 A Enclosure: Type 1 MCB Rating: 125 A
CKT | Circuit Description | Trip | Poles | A |  | B |  | C |  | Poles | Trip | Circuit Description |  | CKT
1 | RCPT SMALL CONFERENCE S101A N, S | 20 A | 1 | 900 | 750 |  |  |  |  | 1 | 20 A | VAV-ZONE-ISAC |  | 2
3 | RCPT CONFERENCE S101A | 20 A | 1 |  |  | 1110 | 180 |  |  | 1 | 20 A | RCPT ROOFTOP SERVICE |  | 4
5 | RCPT SPACE ISAC RECEPTION S101 | 20 A | 1 |  |  |  |  | 1220 | 0 | 1 | 20 A | SPARE |  | 6
7 | RCPT SPACE ISAC RECEPTION S101 | 20 A | 1 | 970 | 0 |  |  |  |  | 1 | 20 A | SPARE |  | 8
9 | RCPT OFFICE S108D, S108E | 20 A | 1 |  |  | 1120 | 0 |  |  | 1 | 20 A | SPARE |  | 10
11 | RCPT OFFICE S108C, S108B | 20 A | 1 |  |  |  |  | 1120 | 0 | 1 | 20 A | SPARE |  | 12
13 | RCPT CIRCULATION S108 S109 | 20 A | 1 | 720 | 0 |  |  |  |  | 1 | 20 A | SPARE |  | 14
15 | SPARE | 20 A | 1 |  |  | 0 | 0 |  |  | -- | -- | SPACE |  | 16
17 | SPARE | 20 A | 1 |  |  |  |  | 0 | 0 | -- | -- | SPACE |  | 18
19 | SPARE | 20 A | 1 | 0 | 0 |  |  |  |  | -- | -- | SPACE |  | 20
21 | SPARE | 20 A | 1 |  |  | 0 | 0 |  |  | -- | -- | SPACE |  | 22
23 | SPARE | 20 A | 1 |  |  |  |  | 0 | 0 | -- | -- | SPACE |  | 24
25 | SPACE | -- | -- | 0 | 0 |  |  |  |  | -- | -- | SPACE |  | 26
27 | SPACE | -- | -- |  |  | 0 | 0 |  |  | -- | -- | SPACE |  | 28
29 | SPACE | -- | -- |  |  |  |  | 0 | 0 | -- | -- | SPACE |  | 30
31 | SPACE | -- | -- | 0 | 0 |  |  |  |  | -- | -- | SPACE |  | 32
33 | SPACE | -- | -- |  |  | 0 | 0 |  |  | -- | -- | SPACE |  | 34
35 | SPACE | -- | -- |  |  |  |  | 0 | 0 | -- | -- | SPACE |  | 36
37 | SPACE | -- | -- | 0 | 0 |  |  |  |  | -- | -- | SPACE |  | 38
39 | SPACE | -- | -- |  |  | 0 | 0 |  |  | -- | -- | SPACE |  | 40
41 | SPACE | -- | -- |  |  |  |  | 0 | 0 | -- | -- | SPACE |  | 42
Total Load: 3340 VA 2410 VA 2340 VA Total Amps: 28 A 20 A 20 A |  |  |  | 3340 VA |  | 2410 VA |  | 2340 VA
Load Classification |  | Connected Load |  |  | Demand Factor |  |  | Estimated Demand |  |  | Panel Totals
Receptacle |  | 5040 VA |  |  | 100.00% |  |  | 5040 VA
Power |  | 2300 VA |  |  | 100.00% |  |  | 2300 VA |  |  | Total Conn. Load: |  | 8090 VA
Mechanical Equipment |  | 750 VA |  |  | 125.00% |  |  | 938 VA |  |  | Total Est. Demand: |  | 8278 VA
[11 empty] | Total Conn.: |  | 22 A
[11 empty] | Total Est. Demand: |  | 23 A
Notes:

## ELECTRICAL_PANELBOAR_6
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Panelboard: UCCSLD Location: ELEC. N140 Volts: 208Y/120 A.I.C. Rating: REFER TO FAULT CALCULATIONS Supply From: UCCSLC Phases: 3 Mains Type: MLO Mounting: Surface Wires: 4 Bus Rating: 225 A Enclosure: Type 1
CKT | Circuit Description | Trip | Poles | A (VA) |  | B (VA) |  | C (VA) |  | Poles | Trip | Circuit Description |  | CKT
1 | RCPT WORKSTATIONS CYBER RANGE LAB... | 20 A | 1 | 1500 | 1000 |  |  |  |  | 1 | 20 A | RCPT W CLASSROOM N106 |  | 2
3 | RCPT WORKSTATIONS CYBER RANGE LAB... | 20 A | 1 |  |  | 1500 | 1000 |  |  | 1 | 20 A | RCPT E CLASSROOM N106 |  | 4
5 | RCPT WORKSTATIONS CYBER RANGE LAB... | 20 A | 1 |  |  |  |  | 1500 | 1000 | 1 | 20 A | RCPT FLOOR BOX CLASSROOM N106 |  | 6
7 | RCPT WORKSTATIONS CYBER RANGE LAB... | 20 A | 1 | 1500 | 500 |  |  |  |  | 1 | 20 A | RCPT FLOOR BOX CLASSROOM N106 |  | 8
9 | RCPT WORKSTATIONS CYBER RANGE LAB... | 20 A | 1 |  |  | 1000 | 500 |  |  | 1 | 20 A | RCPT FLOOR BOX CLASSROOM N106 |  | 10
11 | RCPT CYBER RANGE LAB N111, COLLAB... | 20 A | 1 |  |  |  |  | 900 | 500 | 1 | 20 A | RCPT FLOOR BOX CLASSROOM N106 |  | 12
13 | RCPT WORKSTATIONS COMPUTER LAB N112 | 20 A | 1 | 1500 | 720 |  |  |  |  | 1 | 20 A | RCPT CLASSROOM N106 |  | 14
15 | RCPT WORKSTATIONS COMPUTER LAB N112 | 20 A | 1 |  |  | 680 | 900 |  |  | 1 | 20 A | RCPT PROJECTOR CLASSROOM N106 |  | 16
17 | RCPT WORKSTATIONS COMPUTER LAB N112 | 20 A | 1 |  |  |  |  | 860 | 600 | 1 | 20 A | PROJECTION SCREEN CLASSROOM N106 |  | 18
19 | RCPT WORKSTATIONS COMPUTER LAB N112 | 20 A | 1 | 1500 | 900 |  |  |  |  | 1 | 20 A | RCPT COLLAB SE CIRCULATION N119 |  | 20
21 | RCPT WORKSTATIONS COMPUTER LAB N112 | 20 A | 1 |  |  | 500 | 0 |  |  | 1 | 20 A | SPARE |  | 22
23 | RCPT WORKSTATIONS COMPUTER LAB N112 | 20 A | 1 |  |  |  |  | 500 | 0 | 1 | 20 A | SPARE |  | 24
25 | RCPT WORKSTATIONS COMPUTER LAB N112 | 20 A | 1 | 500 | 0 |  |  |  |  | 1 | 20 A | SPARE |  | 26
27 | RCPT WORKSTATIONS COMPUTER LAB N112 | 20 A | 1 |  |  | 1000 | 0 |  |  | 1 | 20 A | SPARE |  | 28
29 | RCPT PROJECTOR COMPUTER LAB N112 | 20 A | 1 |  |  |  |  | 900 | 0 | 1 | 20 A | SPARE |  | 30
31 | RCPT COMPUTER LAB N112, COLLAB N107C | 20 A | 1 | 900 | 0 |  |  |  |  | 1 | 20 A | SPARE |  | 32
33 | RCPT COLLAB N107A, CLASSROOM N106 | 20 A | 1 |  |  | 900 | 0 |  |  | -- | -- | SPACE |  | 34
35 | RCPT COLLAB N113A, JAN N108, TOILET N109 | 20 A | 1 |  |  |  |  | 900 | 0 | -- | -- | SPACE |  | 36
37 | SPARE | 20 A | 1 | 0 | 0 |  |  |  |  | -- | -- | SPACE |  | 38
39 | SPARE | 20 A | 1 |  |  | 0 | 0 |  |  | -- | -- | SPACE |  | 40
41 | SPARE | 20 A | 1 |  |  |  |  | 0 | 0 | -- | -- | SPACE |  | 42
Total Load: 10520 VA 7980 VA 7660 VA Total Amps: 88 A 67 A 64 A |  |  |  | 10520 VA |  | 7980 VA |  | 7660 VA
Load Classification |  | Connected Load |  |  | Demand Factor |  |  | Estimated Demand |  |  | Panel Totals
Power |  | 18400 VA |  |  | 100.00% |  |  | 18400 VA
Receptacle |  | 7760 VA |  |  | 100.00% |  |  | 7760 VA |  |  | Total Conn. Load: |  | 26160 VA
[11 empty] | Total Est. Demand: |  | 26160 VA
[11 empty] | Total Conn.: |  | 73 A
[11 empty] | Total Est. Demand: |  | 73 A
Notes:

## SECURITY_SYMBOLS_LEG_0
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
SECURITY CAMERA SCHEDULE
ROOM NUMBER | ROOM NAME | DEVICE NUMBER | CAMERA TYPE | MAKE & MODEL | TERMINATION POINT | REFERENCE DETAIL | NOTES
|  | C-EXTERIOR-1 | FIX | 4MP EXTERIOR | DATA N124 | 7/Y8.1.1 | CAMERA BY OWNER
|  | C-EXTERIOR-2 | FIX | 4MP EXTERIOR | DATA N124 | 7/Y8.1.1 | CAMERA BY OWNER
E-180B | VEST | C-E-180B-1 | FIX | 1080P | DATA N124 | 6/Y8.1.1 | CAMERA BY OWNER
N103 | CAFE | C-N103-1 | 360 | FISHEYE 360 | DATA N124 | 6/Y8.1.1 | CAMERA BY OWNER
N119 | CIRCULATION | C-N119-1 | 360 | FISHEYE 360 | DATA N124 | 6/Y8.1.1 | CAMERA BY OWNER
N119 | CIRCULATION | C-N119-2 | 360 | FISHEYE 360 | DATA N124 | 5/Y8.1.1 | CAMERA BY OWNER
N122 | Space | C-N119-3 | 180 | FISHEYE 180 | DATA N124 | 6/Y8.1.1 | CAMERA BY OWNER
S100 | EAST CORRIDOR | C-S100-1 | 180 | FISHEYE 180 | DATA N124 | 4/Y8.1.1 | CAMERA BY OWNER
S101 | SPACE ISAC RECEPTION | C-S101-1 | FIX | 1080P | DATA/SERVER S103 | 4/Y8.1.1 | CAMERA BY OWNER
S102 | CYBER VULNERABILITY LAB | C-S102-1 | FIX | 1080P | DATA/SERVER S103 | 4/Y8.1.1 | CAMERA BY OWNER
S103 | DATA/SERVER | C-S103-1 | FIX | 1080P | DATA/SERVER S103 | 4/Y8.1.1 | CAMERA BY OWNER
S107 | WATCH CENTER | C-S107-1 | FIX | 1080P | DATA/SERVER S103 | 5/Y8.1.1 | CAMERA BY OWNER
S108 | CIRCULATION | C-S108-1 | FIX | 1080P | DATA/SERVER S103 | 5/Y8.1.1 | CAMERA BY OWNER

## SECURITY_SYMBOLS_LEG_1
0 | 1 | 2 | 3 | 4
SECURITY SYMBOLS LEGEND
(THIS IS A MASTER LEGEND, NOT ALL SYMBOLS MAY APPEAR ON DRAWINGS.)
SECURITY DEVICES
SYMBOL |  | DESCRIPTION
XX XX |  | WALL MOUNTED DEVICE CEILING MOUNTED DEVICE
SECURITY DEVICE DESIGNATORS
DEVICE NUMBER -REFER TO THE SECURITY D-####-# DEVICE SCHEDULE FOR MORE INFORMATION. DEVICE TYPE XX ADDITIONAL INFORMATION X
DEVICE TYPES
ACP ACCESS CONTROL PANEL IL INTER-LOCK T TICKET CB CODE BLUE PHONE LA LOCAL ALARM TS1 TURNSTILE -ADA GB GLASS BREAK DETECTOR MS MOTION SENSOR TS2 TURNSTILE IC INTERCOM NVR NETWORK VIDEO RECORDER WR WIRELESS RECEIVER ICM INTERCOM MASTER P PANIC DEVICE WS WORKSTATION PS POWER SUPPLY
ADDITIONAL INFORMATION
FA FIRE ALARM TIE IN W WIRELESS G GATE MOUNTED ADA WITH ADA OPENERS
SECURITY CAMERAS |  |  | SECURITY CAMERAS
SYMBOL | DESCRIPTION |  | SYMBOL | DESCRIPTION
FIX PTZ DUO DUO | FIXED CAMERA PTZ CAMERA 90° DUO CAMERA 180° DUO CAMERA |  | 180 270 360 | 180° CAMERA 270° CAMERA 360° CAMERA
SECURITY CAMERA DESIGNATORS
CAMERA NUMBER -REFER TO THE SECURITY C-####-# CAMERA SCHEDULE FOR MORE INFORMATION. CAMERA TYPE XX
SECURITY DOORS
SYMBOL |  | DESCRIPTION
XX |  | ACCESS CONTROL TYPE ASSOCIATED DEVICE LOCATION
SECURITY DOOR DESIGNATORS
DOOR NUMBER -REFER TO THE SECURITY DOOR SCHEDULE FOR MORE INFORMATION. #### XX ACCESS CONTROL TYPE ASSOCIATED DEVICE LOCATION
ADDITIONAL INFORMATION
CR CARD READER DOOR EC ELEC LOCK CONTROL ML MANUAL LOCK DC DOOR CONTACT FR FUTURE CARD READER

## SECURITY_SYMBOLS_LEG_2
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
SECURITY DEVICE SCHEDULE
ROOM NUMBER | ROOM NAME | DEVICE NUMBER | DEVICE TYPE | MAKE | TERMINATION POINT | REFERENCE DETAIL | NOTES
N124 | DATA ROOM | ACP-N124-1 | ACP | - | N124 | - | ACCESS CONTROL SYSTEM BY OWNER
N124 | DATA ROOM | NVR-N124-1 | NVR | - | N124 | - | VIDEO SURVEILLANCE SYSTEM BY OWNER
N124 | DATA ROOM | PS-N124-1 | PS | - | N124 | - | ACCESS CONTROL SYSTEM BY OWNER
S103 | DATA/SERVER | ACP-S103-1 | ACP | - | S103 | - | ACCESS CONTROL SYSTEM BY OWNER
S103 | DATA/SERVER | PS-S103-1 | PS | - | S103 | - | ACCESS CONTROL SYSTEM BY OWNER

## SECURITY_SYMBOLS_LEG_3
0 | 1 | 2 | 3 | 4 | 5 | 6
SECURITY DOOR SCHEDULE
ROOM NUMBER | ROOM NAME | DOOR NUMBER | ACCESS CONTROL | TERMINATION POINT | REFERENCE DETAIL | NOTES
E-180B | VEST | 135 | CR | DATA N124 | 1/Y8.1.1 | ACCESS CONTROL DEVICES BY OWNER
N101 | VESTIBULE | N101A | CR | DATA N124 | 1/Y8.1.1 | ACCESS CONTROL DEVICES BY OWNER
N124 | DATA ROOM | N124 | CR | DATA N124 | 2/Y8.1.1 | ACCESS CONTROL DEVICES BY OWNER
S101 | SPACE ISAC RECEPTION | S101 | CR | DATA/SERVER S103 | 2/Y8.1.1 | ACCESS CONTROL DEVICES BY OWNER
S102 | CYBER VULNERABILITY LAB | S102C | CR | DATA/SERVER S103 | 2/Y8.1.1 | ACCESS CONTROL DEVICES BY OWNER
S102A | CVL VESTIBULE | S102A | CR | DATA/SERVER S103 | 2/Y8.1.1 | ACCESS CONTROL DEVICES BY OWNER
S103 | DATA/SERVER | S103 | CR | DATA/SERVER S103 | 2/Y8.1.1 | ACCESS CONTROL DEVICES BY OWNER
S107 | WATCH CENTER | S107A | CR | DATA/SERVER S103 | 2/Y8.1.1 | ACCESS CONTROL DEVICES BY OWNER
S107 | WATCH CENTER | S107B | CR | DATA/SERVER S103 | 2/Y8.1.1 | ACCESS CONTROL DEVICES BY OWNER
S108 | CIRCULATION | S108 | CR | DATA/SERVER S103 | 1/Y8.1.1 | ACCESS CONTROL DEVICES BY OWNER
S108 | CIRCULATION | S108A | CR | DATA/SERVER S103 | 1/Y8.1.1 | ACCESS CONTROL DEVICES BY OWNER
S109 | CIRCULATION | S109 | CR | DATA/SERVER S103 | 2/Y8.1.1 | ACCESS CONTROL DEVICES BY OWNER

## SECURITY_SYMBOLS_LEG_4
0 | 1
SHEET INDEX
SHEET NUMBER | SHEET DESCRIPTION
Y0.0.1 | SECURITY SYMBOLS LEGEND, NOTES AND SCHEDULES
Y1.1.2 | SECURITY - LEVEL 1 - PLAN - NORTH - AREA A
Y1.1.3 | SECURITY - LEVEL 1 - PLAN - NORTH - AREA B
Y1.1.4 | SECURITY - LEVEL 1 - PLAN - SOUTH - AREA A
Y8.1.1 | SECURITY DETAILS